## Introduction
Smappee Infinity Modbus energy meter
This document describes the Modbus RTU (RS-485) interface of the Smappee Infinity Modbus energy meter.
Modbus RTU (RS-485) interface:
Type: | Multidrop, bidirectional
Connections: | 2-wire, maximum distance 1,000 m
Addresses: | 247 addresses, default address 61, auto-assigned in case of multiple devices
Protocol: | Modbus RTU
Data format: | 1 start bit, 8 data bit, no parity, 1 stop bit
Baud-rate: | 38.400 or 115.200 bit/ sec (auto-detect)
Driver input impedance: | 1/8 unit load, maximum 256 transceivers on the same bus
Insulation: | 3240 V AC RS-485 bus to mains input
© 2020 Smappee. All rights reserved.
Document date | 2026-03-10

## Encoding
Encoding
Following data types are encoded as modbus holding registers:
Int16: | 16bit integer, single register, big endian (Most Significant Byte first)
Int32: | 32bit integer encoded in two consecutive registers, first register contains low word (low 16 bits), second register high word (high 16 bits)
Float: | Single precision IEEE floating point encoded in two consecutive registers, first register contains low word , second register high word
Complex: | Encoded in 4 consecutive registers as 2 floats representing real and imaginary part of complex number
Supported modbus commands:
Read Holding Registers: | Function code 3
Write Multiple Registers: | Function code 16

## Index
Index
1 | Voltages
2 | Currents
3 | Powers
4 | Virtual Channel Powers
5 | Energy
6 | Virtual Channel Energy
7 | Frequency
8 | Harmonics
9 | General Configuration
10 | CT Configuration
11 | Virtual Channel Configuration
12 | Bus Info
13 | Bus Diagnostics

## Voltages
Modbus Address | Modbus Address (Hex) | Size | Type | Phase | Unit | R/W | Description
0 | 0x0000 | 2 | Float | L1-N | Volt | R | Root Mean Square Voltage, 1 second average
2 | 0x0002 | 2 | Float | L1-N | Volt | R | Root Mean Square Fundamental Voltage, 1 second average
4 | 0x0004 | 2 | Float | L2-N | Volt | R | Root Mean Square Voltage, 1 second average
6 | 0x0006 | 2 | Float | L2-N | Volt | R | Root Mean Square Fundamental Voltage, 1 second average
8 | 0x0008 | 2 | Float | L3-N | Volt | R | Root Mean Square Voltage, 1 second average
10 | 0x000A | 2 | Float | L3-N | Volt | R | Root Mean Square Fundamental Voltage, 1 second average
12 | 0x000C | 2 | Float | L1-L2 | Volt | R | Root Mean Square Voltage, 1 second average
14 | 0x000E | 2 | Float | L1-L2 | Volt | R | Root Mean Square Fundamental Voltage, 1 second average
16 | 0x0010 | 2 | Float | L2-L3 | Volt | R | Root Mean Square Voltage, 1 second average
18 | 0x0012 | 2 | Float | L2-L3 | Volt | R | Root Mean Square Fundamental Voltage, 1 second average
20 | 0x0014 | 2 | Float | L3-L1 | Volt | R | Root Mean Square Voltage, 1 second average
22 | 0x0016 | 2 | Float | L3-L1 | Volt | R | Root Mean Square Fundamental Voltage, 1 second average
24 | 0x0018 | 2 | Float | L1-N | Volt | R | Root Mean Square Third harmonic voltage, 1 second average
26 | 0x001A | 2 | Float | L2-N | Volt | R | Root Mean Square Third harmonic voltage, 1 second average
28 | 0x001C | 2 | Float | L3-N | Volt | R | Root Mean Square Third harmonic voltage, 1 second average
30 | 0x001E | 2 | Float | L1-L2 | Volt | R | Root Mean Square Third harmonic voltage, 1 second average
32 | 0x0020 | 2 | Float | L2-L3 | Volt | R | Root Mean Square Third harmonic voltage, 1 second average
34 | 0x0022 | 2 | Float | L3-L1 | Volt | R | Root Mean Square Third harmonic voltage, 1 second average
36 | 0x0024 | 2 | Float | L1-N | Volt | R | Root Mean Square Fifth harmonic voltage, 1 second average
38 | 0x0026 | 2 | Float | L2-N | Volt | R | Root Mean Square Fifth harmonic voltage, 1 second average
40 | 0x0028 | 2 | Float | L3-N | Volt | R | Root Mean Square Fifth harmonic voltage, 1 second average
42 | 0x002A | 2 | Float | L1-L2 | Volt | R | Root Mean Square Fifth harmonic voltage, 1 second average
44 | 0x002C | 2 | Float | L2-L3 | Volt | R | Root Mean Square Fifth harmonic voltage, 1 second average
46 | 0x002E | 2 | Float | L3-L1 | Volt | R | Root Mean Square Fifth harmonic voltage, 1 second average

## Currents
Modbus Address | Modbus Address (Hex) | Size | Type | Channel | Unit | R/W | Description
128 | 0x0080 | 2 | Float | 0 | Ampere | R | Root Mean Square Current, 1 second average
130 | 0x0082 | 2 | Float | 0 | Ampere | R | Root Mean Square Fundamental Current, 1 second average
132 | 0x0084 | 2 | Float | 1 | Ampere | R | Root Mean Square Current, 1 second average
134 | 0x0086 | 2 | Float | 1 | Ampere | R | Root Mean Square Fundamental Current, 1 second average
136 | 0x0088 | 2 | Float | 2 | Ampere | R | Root Mean Square Current, 1 second average
138 | 0x008A | 2 | Float | 2 | Ampere | R | Root Mean Square Fundamental Current, 1 second average
140 | 0x008C | 2 | Float | 3 | Ampere | R | Root Mean Square Current, 1 second average
142 | 0x008E | 2 | Float | 3 | Ampere | R | Root Mean Square Fundamental Current, 1 second average
144 | 0x0090 | 2 | Float | 4 | Ampere | R | Root Mean Square Current, 1 second average
146 | 0x0092 | 2 | Float | 4 | Ampere | R | Root Mean Square Fundamental Current, 1 second average
148 | 0x0094 | 2 | Float | 5 | Ampere | R | Root Mean Square Current, 1 second average
150 | 0x0096 | 2 | Float | 5 | Ampere | R | Root Mean Square Fundamental Current, 1 second average
152 | 0x0098 | 2 | Float | 6 | Ampere | R | Root Mean Square Current, 1 second average
154 | 0x009A | 2 | Float | 6 | Ampere | R | Root Mean Square Fundamental Current, 1 second average
156 | 0x009C | 2 | Float | 7 | Ampere | R | Root Mean Square Current, 1 second average
158 | 0x009E | 2 | Float | 7 | Ampere | R | Root Mean Square Fundamental Current, 1 second average
160 | 0x00A0 | 2 | Float | 8 | Ampere | R | Root Mean Square Current, 1 second average
162 | 0x00A2 | 2 | Float | 8 | Ampere | R | Root Mean Square Fundamental Current, 1 second average
164 | 0x00A4 | 2 | Float | 9 | Ampere | R | Root Mean Square Current, 1 second average
166 | 0x00A6 | 2 | Float | 9 | Ampere | R | Root Mean Square Fundamental Current, 1 second average
168 | 0x00A8 | 2 | Float | 10 | Ampere | R | Root Mean Square Current, 1 second average
170 | 0x00AA | 2 | Float | 10 | Ampere | R | Root Mean Square Fundamental Current, 1 second average
172 | 0x00AC | 2 | Float | 11 | Ampere | R | Root Mean Square Current, 1 second average
174 | 0x00AE | 2 | Float | 11 | Ampere | R | Root Mean Square Fundamental Current, 1 second average
176 | 0x00B0 | 2 | Float | 12 | Ampere | R | Root Mean Square Current, 1 second average
178 | 0x00B2 | 2 | Float | 12 | Ampere | R | Root Mean Square Fundamental Current, 1 second average
180 | 0x00B4 | 2 | Float | 13 | Ampere | R | Root Mean Square Current, 1 second average
182 | 0x00B6 | 2 | Float | 13 | Ampere | R | Root Mean Square Fundamental Current, 1 second average
184 | 0x00B8 | 2 | Float | 14 | Ampere | R | Root Mean Square Current, 1 second average
186 | 0x00BA | 2 | Float | 14 | Ampere | R | Root Mean Square Fundamental Current, 1 second average
188 | 0x00BC | 2 | Float | 15 | Ampere | R | Root Mean Square Current, 1 second average
190 | 0x00BE | 2 | Float | 15 | Ampere | R | Root Mean Square Fundamental Current, 1 second average
192 | 0x00C0 | 2 | Float | 16 | Ampere | R | Root Mean Square Current, 1 second average
194 | 0x00C2 | 2 | Float | 16 | Ampere | R | Root Mean Square Fundamental Current, 1 second average
196 | 0x00C4 | 2 | Float | 17 | Ampere | R | Root Mean Square Current, 1 second average
198 | 0x00C6 | 2 | Float | 17 | Ampere | R | Root Mean Square Fundamental Current, 1 second average
200 | 0x00C8 | 2 | Float | 18 | Ampere | R | Root Mean Square Current, 1 second average
202 | 0x00CA | 2 | Float | 18 | Ampere | R | Root Mean Square Fundamental Current, 1 second average
204 | 0x00CC | 2 | Float | 19 | Ampere | R | Root Mean Square Current, 1 second average
206 | 0x00CE | 2 | Float | 19 | Ampere | R | Root Mean Square Fundamental Current, 1 second average
208 | 0x00D0 | 2 | Float | 20 | Ampere | R | Root Mean Square Current, 1 second average
210 | 0x00D2 | 2 | Float | 20 | Ampere | R | Root Mean Square Fundamental Current, 1 second average
212 | 0x00D4 | 2 | Float | 21 | Ampere | R | Root Mean Square Current, 1 second average
214 | 0x00D6 | 2 | Float | 21 | Ampere | R | Root Mean Square Fundamental Current, 1 second average
216 | 0x00D8 | 2 | Float | 22 | Ampere | R | Root Mean Square Current, 1 second average
218 | 0x00DA | 2 | Float | 22 | Ampere | R | Root Mean Square Fundamental Current, 1 second average
220 | 0x00DC | 2 | Float | 23 | Ampere | R | Root Mean Square Current, 1 second average
222 | 0x00DE | 2 | Float | 23 | Ampere | R | Root Mean Square Fundamental Current, 1 second average
224 | 0x00E0 | 2 | Float | 24 | Ampere | R | Root Mean Square Current, 1 second average
226 | 0x00E2 | 2 | Float | 24 | Ampere | R | Root Mean Square Fundamental Current, 1 second average
228 | 0x00E4 | 2 | Float | 25 | Ampere | R | Root Mean Square Current, 1 second average
230 | 0x00E6 | 2 | Float | 25 | Ampere | R | Root Mean Square Fundamental Current, 1 second average
232 | 0x00E8 | 2 | Float | 26 | Ampere | R | Root Mean Square Current, 1 second average
234 | 0x00EA | 2 | Float | 26 | Ampere | R | Root Mean Square Fundamental Current, 1 second average
236 | 0x00EC | 2 | Float | 27 | Ampere | R | Root Mean Square Current, 1 second average
238 | 0x00EE | 2 | Float | 27 | Ampere | R | Root Mean Square Fundamental Current, 1 second average

## Powers
Modbus Address | Modbus Address (Hex) | Size | Type | Channel | Unit | R/W | Description
256 | 0x0100 | 2 | Float | 0 | Watt | R | Total Active Power, 1 second average
258 | 0x0102 | 2 | Float | 0 | Watt | R | Fundamental Active Power, 1 second average
260 | 0x0104 | 2 | Float | 1 | Watt | R | Total Active Power, 1 second average
262 | 0x0106 | 2 | Float | 1 | Watt | R | Fundamental Active Power, 1 second average
264 | 0x0108 | 2 | Float | 2 | Watt | R | Total Active Power, 1 second average
266 | 0x010A | 2 | Float | 2 | Watt | R | Fundamental Active Power, 1 second average
268 | 0x010C | 2 | Float | 3 | Watt | R | Total Active Power, 1 second average
270 | 0x010E | 2 | Float | 3 | Watt | R | Fundamental Active Power, 1 second average
272 | 0x0110 | 2 | Float | 4 | Watt | R | Total Active Power, 1 second average
274 | 0x0112 | 2 | Float | 4 | Watt | R | Fundamental Active Power, 1 second average
276 | 0x0114 | 2 | Float | 5 | Watt | R | Total Active Power, 1 second average
278 | 0x0116 | 2 | Float | 5 | Watt | R | Fundamental Active Power, 1 second average
280 | 0x0118 | 2 | Float | 6 | Watt | R | Total Active Power, 1 second average
282 | 0x011A | 2 | Float | 6 | Watt | R | Fundamental Active Power, 1 second average
284 | 0x011C | 2 | Float | 7 | Watt | R | Total Active Power, 1 second average
286 | 0x011E | 2 | Float | 7 | Watt | R | Fundamental Active Power, 1 second average
288 | 0x0120 | 2 | Float | 8 | Watt | R | Total Active Power, 1 second average
290 | 0x0122 | 2 | Float | 8 | Watt | R | Fundamental Active Power, 1 second average
292 | 0x0124 | 2 | Float | 9 | Watt | R | Total Active Power, 1 second average
294 | 0x0126 | 2 | Float | 9 | Watt | R | Fundamental Active Power, 1 second average
296 | 0x0128 | 2 | Float | 10 | Watt | R | Total Active Power, 1 second average
298 | 0x012A | 2 | Float | 10 | Watt | R | Fundamental Active Power, 1 second average
300 | 0x012C | 2 | Float | 11 | Watt | R | Total Active Power, 1 second average
302 | 0x012E | 2 | Float | 11 | Watt | R | Fundamental Active Power, 1 second average
304 | 0x0130 | 2 | Float | 12 | Watt | R | Total Active Power, 1 second average
306 | 0x0132 | 2 | Float | 12 | Watt | R | Fundamental Active Power, 1 second average
308 | 0x0134 | 2 | Float | 13 | Watt | R | Total Active Power, 1 second average
310 | 0x0136 | 2 | Float | 13 | Watt | R | Fundamental Active Power, 1 second average
312 | 0x0138 | 2 | Float | 14 | Watt | R | Total Active Power, 1 second average
314 | 0x013A | 2 | Float | 14 | Watt | R | Fundamental Active Power, 1 second average
316 | 0x013C | 2 | Float | 15 | Watt | R | Total Active Power, 1 second average
318 | 0x013E | 2 | Float | 15 | Watt | R | Fundamental Active Power, 1 second average
320 | 0x0140 | 2 | Float | 16 | Watt | R | Total Active Power, 1 second average
322 | 0x0142 | 2 | Float | 16 | Watt | R | Fundamental Active Power, 1 second average
324 | 0x0144 | 2 | Float | 17 | Watt | R | Total Active Power, 1 second average
326 | 0x0146 | 2 | Float | 17 | Watt | R | Fundamental Active Power, 1 second average
328 | 0x0148 | 2 | Float | 18 | Watt | R | Total Active Power, 1 second average
330 | 0x014A | 2 | Float | 18 | Watt | R | Fundamental Active Power, 1 second average
332 | 0x014C | 2 | Float | 19 | Watt | R | Total Active Power, 1 second average
334 | 0x014E | 2 | Float | 19 | Watt | R | Fundamental Active Power, 1 second average
336 | 0x0150 | 2 | Float | 20 | Watt | R | Total Active Power, 1 second average
338 | 0x0152 | 2 | Float | 20 | Watt | R | Fundamental Active Power, 1 second average
340 | 0x0154 | 2 | Float | 21 | Watt | R | Total Active Power, 1 second average
342 | 0x0156 | 2 | Float | 21 | Watt | R | Fundamental Active Power, 1 second average
344 | 0x0158 | 2 | Float | 22 | Watt | R | Total Active Power, 1 second average
346 | 0x015A | 2 | Float | 22 | Watt | R | Fundamental Active Power, 1 second average
348 | 0x015C | 2 | Float | 23 | Watt | R | Total Active Power, 1 second average
350 | 0x015E | 2 | Float | 23 | Watt | R | Fundamental Active Power, 1 second average
352 | 0x0160 | 2 | Float | 24 | Watt | R | Total Active Power, 1 second average
354 | 0x0162 | 2 | Float | 24 | Watt | R | Fundamental Active Power, 1 second average
356 | 0x0164 | 2 | Float | 25 | Watt | R | Total Active Power, 1 second average
358 | 0x0166 | 2 | Float | 25 | Watt | R | Fundamental Active Power, 1 second average
360 | 0x0168 | 2 | Float | 26 | Watt | R | Total Active Power, 1 second average
362 | 0x016A | 2 | Float | 26 | Watt | R | Fundamental Active Power, 1 second average
364 | 0x016C | 2 | Float | 27 | Watt | R | Total Active Power, 1 second average
366 | 0x016E | 2 | Float | 27 | Watt | R | Fundamental Active Power, 1 second average
384 | 0x0180 | 2 | Float | 0 | var | R | Total Reactive Power, 1 second average
386 | 0x0182 | 2 | Float | 0 | var | R | Fundamental Reactive Power, 1 second average
388 | 0x0184 | 2 | Float | 1 | var | R | Total Reactive Power, 1 second average
390 | 0x0186 | 2 | Float | 1 | var | R | Fundamental Reactive Power, 1 second average
392 | 0x0188 | 2 | Float | 2 | var | R | Total Reactive Power, 1 second average
394 | 0x018A | 2 | Float | 2 | var | R | Fundamental Reactive Power, 1 second average
396 | 0x018C | 2 | Float | 3 | var | R | Total Reactive Power, 1 second average
398 | 0x018E | 2 | Float | 3 | var | R | Fundamental Reactive Power, 1 second average
400 | 0x0190 | 2 | Float | 4 | var | R | Total Reactive Power, 1 second average
402 | 0x0192 | 2 | Float | 4 | var | R | Fundamental Reactive Power, 1 second average
404 | 0x0194 | 2 | Float | 5 | var | R | Total Reactive Power, 1 second average
406 | 0x0196 | 2 | Float | 5 | var | R | Fundamental Reactive Power, 1 second average
408 | 0x0198 | 2 | Float | 6 | var | R | Total Reactive Power, 1 second average
410 | 0x019A | 2 | Float | 6 | var | R | Fundamental Reactive Power, 1 second average
412 | 0x019C | 2 | Float | 7 | var | R | Total Reactive Power, 1 second average
414 | 0x019E | 2 | Float | 7 | var | R | Fundamental Reactive Power, 1 second average
416 | 0x01A0 | 2 | Float | 8 | var | R | Total Reactive Power, 1 second average
418 | 0x01A2 | 2 | Float | 8 | var | R | Fundamental Reactive Power, 1 second average
420 | 0x01A4 | 2 | Float | 9 | var | R | Total Reactive Power, 1 second average
422 | 0x01A6 | 2 | Float | 9 | var | R | Fundamental Reactive Power, 1 second average
424 | 0x01A8 | 2 | Float | 10 | var | R | Total Reactive Power, 1 second average
426 | 0x01AA | 2 | Float | 10 | var | R | Fundamental Reactive Power, 1 second average
428 | 0x01AC | 2 | Float | 11 | var | R | Total Reactive Power, 1 second average
430 | 0x01AE | 2 | Float | 11 | var | R | Fundamental Reactive Power, 1 second average
432 | 0x01B0 | 2 | Float | 12 | var | R | Total Reactive Power, 1 second average
434 | 0x01B2 | 2 | Float | 12 | var | R | Fundamental Reactive Power, 1 second average
436 | 0x01B4 | 2 | Float | 13 | var | R | Total Reactive Power, 1 second average
438 | 0x01B6 | 2 | Float | 13 | var | R | Fundamental Reactive Power, 1 second average
440 | 0x01B8 | 2 | Float | 14 | var | R | Total Reactive Power, 1 second average
442 | 0x01BA | 2 | Float | 14 | var | R | Fundamental Reactive Power, 1 second average
444 | 0x01BC | 2 | Float | 15 | var | R | Total Reactive Power, 1 second average
446 | 0x01BE | 2 | Float | 15 | var | R | Fundamental Reactive Power, 1 second average
448 | 0x01C0 | 2 | Float | 16 | var | R | Total Reactive Power, 1 second average
450 | 0x01C2 | 2 | Float | 16 | var | R | Fundamental Reactive Power, 1 second average
452 | 0x01C4 | 2 | Float | 17 | var | R | Total Reactive Power, 1 second average
454 | 0x01C6 | 2 | Float | 17 | var | R | Fundamental Reactive Power, 1 second average
456 | 0x01C8 | 2 | Float | 18 | var | R | Total Reactive Power, 1 second average
458 | 0x01CA | 2 | Float | 18 | var | R | Fundamental Reactive Power, 1 second average
460 | 0x01CC | 2 | Float | 19 | var | R | Total Reactive Power, 1 second average
462 | 0x01CE | 2 | Float | 19 | var | R | Fundamental Reactive Power, 1 second average
464 | 0x01D0 | 2 | Float | 20 | var | R | Total Reactive Power, 1 second average
466 | 0x01D2 | 2 | Float | 20 | var | R | Fundamental Reactive Power, 1 second average
468 | 0x01D4 | 2 | Float | 21 | var | R | Total Reactive Power, 1 second average
470 | 0x01D6 | 2 | Float | 21 | var | R | Fundamental Reactive Power, 1 second average
472 | 0x01D8 | 2 | Float | 22 | var | R | Total Reactive Power, 1 second average
474 | 0x01DA | 2 | Float | 22 | var | R | Fundamental Reactive Power, 1 second average
476 | 0x01DC | 2 | Float | 23 | var | R | Total Reactive Power, 1 second average
478 | 0x01DE | 2 | Float | 23 | var | R | Fundamental Reactive Power, 1 second average
480 | 0x01E0 | 2 | Float | 24 | var | R | Total Reactive Power, 1 second average
482 | 0x01E2 | 2 | Float | 24 | var | R | Fundamental Reactive Power, 1 second average
484 | 0x01E4 | 2 | Float | 25 | var | R | Total Reactive Power, 1 second average
486 | 0x01E6 | 2 | Float | 25 | var | R | Fundamental Reactive Power, 1 second average
488 | 0x01E8 | 2 | Float | 26 | var | R | Total Reactive Power, 1 second average
490 | 0x01EA | 2 | Float | 26 | var | R | Fundamental Reactive Power, 1 second average
492 | 0x01EC | 2 | Float | 27 | var | R | Total Reactive Power, 1 second average
494 | 0x01EE | 2 | Float | 27 | var | R | Fundamental Reactive Power, 1 second average
768 | 0x0300 | 2 | Float | 0 | VA | R | Total Apparent Power, 1 second average
770 | 0x0302 | 2 | Float | 0 | VA | R | Fundamental Apparent Power, 1 second average
772 | 0x0304 | 2 | Float | 1 | VA | R | Total Apparent Power, 1 second average
774 | 0x0306 | 2 | Float | 1 | VA | R | Fundamental Apparent Power, 1 second average
776 | 0x0308 | 2 | Float | 2 | VA | R | Total Apparent Power, 1 second average
778 | 0x030A | 2 | Float | 2 | VA | R | Fundamental Apparent Power, 1 second average
780 | 0x030C | 2 | Float | 3 | VA | R | Total Apparent Power, 1 second average
782 | 0x030E | 2 | Float | 3 | VA | R | Fundamental Apparent Power, 1 second average
784 | 0x0310 | 2 | Float | 4 | VA | R | Total Apparent Power, 1 second average
786 | 0x0312 | 2 | Float | 4 | VA | R | Fundamental Apparent Power, 1 second average
788 | 0x0314 | 2 | Float | 5 | VA | R | Total Apparent Power, 1 second average
790 | 0x0316 | 2 | Float | 5 | VA | R | Fundamental Apparent Power, 1 second average
792 | 0x0318 | 2 | Float | 6 | VA | R | Total Apparent Power, 1 second average
794 | 0x031A | 2 | Float | 6 | VA | R | Fundamental Apparent Power, 1 second average
796 | 0x031C | 2 | Float | 7 | VA | R | Total Apparent Power, 1 second average
798 | 0x031E | 2 | Float | 7 | VA | R | Fundamental Apparent Power, 1 second average
800 | 0x0320 | 2 | Float | 8 | VA | R | Total Apparent Power, 1 second average
802 | 0x0322 | 2 | Float | 8 | VA | R | Fundamental Apparent Power, 1 second average
804 | 0x0324 | 2 | Float | 9 | VA | R | Total Apparent Power, 1 second average
806 | 0x0326 | 2 | Float | 9 | VA | R | Fundamental Apparent Power, 1 second average
808 | 0x0328 | 2 | Float | 10 | VA | R | Total Apparent Power, 1 second average
810 | 0x032A | 2 | Float | 10 | VA | R | Fundamental Apparent Power, 1 second average
812 | 0x032C | 2 | Float | 11 | VA | R | Total Apparent Power, 1 second average
814 | 0x032E | 2 | Float | 11 | VA | R | Fundamental Apparent Power, 1 second average
816 | 0x0330 | 2 | Float | 12 | VA | R | Total Apparent Power, 1 second average
818 | 0x0332 | 2 | Float | 12 | VA | R | Fundamental Apparent Power, 1 second average
820 | 0x0334 | 2 | Float | 13 | VA | R | Total Apparent Power, 1 second average
822 | 0x0336 | 2 | Float | 13 | VA | R | Fundamental Apparent Power, 1 second average
824 | 0x0338 | 2 | Float | 14 | VA | R | Total Apparent Power, 1 second average
826 | 0x033A | 2 | Float | 14 | VA | R | Fundamental Apparent Power, 1 second average
828 | 0x033C | 2 | Float | 15 | VA | R | Total Apparent Power, 1 second average
830 | 0x033E | 2 | Float | 15 | VA | R | Fundamental Apparent Power, 1 second average
832 | 0x0340 | 2 | Float | 16 | VA | R | Total Apparent Power, 1 second average
834 | 0x0342 | 2 | Float | 16 | VA | R | Fundamental Apparent Power, 1 second average
836 | 0x0344 | 2 | Float | 17 | VA | R | Total Apparent Power, 1 second average
838 | 0x0346 | 2 | Float | 17 | VA | R | Fundamental Apparent Power, 1 second average
840 | 0x0348 | 2 | Float | 18 | VA | R | Total Apparent Power, 1 second average
842 | 0x034A | 2 | Float | 18 | VA | R | Fundamental Apparent Power, 1 second average
844 | 0x034C | 2 | Float | 19 | VA | R | Total Apparent Power, 1 second average
846 | 0x034E | 2 | Float | 19 | VA | R | Fundamental Apparent Power, 1 second average
848 | 0x0350 | 2 | Float | 20 | VA | R | Total Apparent Power, 1 second average
850 | 0x0352 | 2 | Float | 20 | VA | R | Fundamental Apparent Power, 1 second average
852 | 0x0354 | 2 | Float | 21 | VA | R | Total Apparent Power, 1 second average
854 | 0x0356 | 2 | Float | 21 | VA | R | Fundamental Apparent Power, 1 second average
856 | 0x0358 | 2 | Float | 22 | VA | R | Total Apparent Power, 1 second average
858 | 0x035A | 2 | Float | 22 | VA | R | Fundamental Apparent Power, 1 second average
860 | 0x035C | 2 | Float | 23 | VA | R | Total Apparent Power, 1 second average
862 | 0x035E | 2 | Float | 23 | VA | R | Fundamental Apparent Power, 1 second average
864 | 0x0360 | 2 | Float | 24 | VA | R | Total Apparent Power, 1 second average
866 | 0x0362 | 2 | Float | 24 | VA | R | Fundamental Apparent Power, 1 second average
868 | 0x0364 | 2 | Float | 25 | VA | R | Total Apparent Power, 1 second average
870 | 0x0366 | 2 | Float | 25 | VA | R | Fundamental Apparent Power, 1 second average
872 | 0x0368 | 2 | Float | 26 | VA | R | Total Apparent Power, 1 second average
874 | 0x036A | 2 | Float | 26 | VA | R | Fundamental Apparent Power, 1 second average
876 | 0x036C | 2 | Float | 27 | VA | R | Total Apparent Power, 1 second average
878 | 0x036E | 2 | Float | 27 | VA | R | Fundamental Apparent Power, 1 second average
896 | 0x0380 | 2 | Float | 0 | Watt | R | Instantaneous Active Power, 100 ms average
898 | 0x0382 | 2 | Float | 1 | Watt | R | Instantaneous Active Power, 100 ms average
900 | 0x0384 | 2 | Float | 2 | Watt | R | Instantaneous Active Power, 100 ms average
902 | 0x0386 | 2 | Float | 3 | Watt | R | Instantaneous Active Power, 100 ms average
904 | 0x0388 | 2 | Float | 4 | Watt | R | Instantaneous Active Power, 100 ms average
906 | 0x038A | 2 | Float | 5 | Watt | R | Instantaneous Active Power, 100 ms average
908 | 0x038C | 2 | Float | 6 | Watt | R | Instantaneous Active Power, 100 ms average
910 | 0x038E | 2 | Float | 7 | Watt | R | Instantaneous Active Power, 100 ms average
912 | 0x0390 | 2 | Float | 8 | Watt | R | Instantaneous Active Power, 100 ms average
914 | 0x0392 | 2 | Float | 9 | Watt | R | Instantaneous Active Power, 100 ms average
916 | 0x0394 | 2 | Float | 10 | Watt | R | Instantaneous Active Power, 100 ms average
918 | 0x0396 | 2 | Float | 11 | Watt | R | Instantaneous Active Power, 100 ms average
920 | 0x0398 | 2 | Float | 12 | Watt | R | Instantaneous Active Power, 100 ms average
922 | 0x039A | 2 | Float | 13 | Watt | R | Instantaneous Active Power, 100 ms average
924 | 0x039C | 2 | Float | 14 | Watt | R | Instantaneous Active Power, 100 ms average
926 | 0x039E | 2 | Float | 15 | Watt | R | Instantaneous Active Power, 100 ms average
928 | 0x03A0 | 2 | Float | 16 | Watt | R | Instantaneous Active Power, 100 ms average
930 | 0x03A2 | 2 | Float | 17 | Watt | R | Instantaneous Active Power, 100 ms average
932 | 0x03A4 | 2 | Float | 18 | Watt | R | Instantaneous Active Power, 100 ms average
934 | 0x03A6 | 2 | Float | 19 | Watt | R | Instantaneous Active Power, 100 ms average
936 | 0x03A8 | 2 | Float | 20 | Watt | R | Instantaneous Active Power, 100 ms average
938 | 0x03AA | 2 | Float | 21 | Watt | R | Instantaneous Active Power, 100 ms average
940 | 0x03AC | 2 | Float | 22 | Watt | R | Instantaneous Active Power, 100 ms average
942 | 0x03AE | 2 | Float | 23 | Watt | R | Instantaneous Active Power, 100 ms average
944 | 0x03B0 | 2 | Float | 24 | Watt | R | Instantaneous Active Power, 100 ms average
946 | 0x03B2 | 2 | Float | 25 | Watt | R | Instantaneous Active Power, 100 ms average
948 | 0x03B4 | 2 | Float | 26 | Watt | R | Instantaneous Active Power, 100 ms average
950 | 0x03B6 | 2 | Float | 27 | Watt | R | Instantaneous Active Power, 100 ms average

## Virtual Channel Powers
Modbus Address | Modbus Address (Hex) | Size | Type | Virtual channel | Unit | R/W | Description
512 | 0x0200 | 2 | Float | 0 | Watt | R | Total Active Power, 1 second average
514 | 0x0202 | 2 | Float | 0 | Watt | R | Fundamental Active Power, 1 second average
516 | 0x0204 | 2 | Float | 1 | Watt | R | Total Active Power, 1 second average
518 | 0x0206 | 2 | Float | 1 | Watt | R | Fundamental Active Power, 1 second average
520 | 0x0208 | 2 | Float | 2 | Watt | R | Total Active Power, 1 second average
522 | 0x020A | 2 | Float | 2 | Watt | R | Fundamental Active Power, 1 second average
524 | 0x020C | 2 | Float | 3 | Watt | R | Total Active Power, 1 second average
526 | 0x020E | 2 | Float | 3 | Watt | R | Fundamental Active Power, 1 second average
528 | 0x0210 | 2 | Float | 4 | Watt | R | Total Active Power, 1 second average
530 | 0x0212 | 2 | Float | 4 | Watt | R | Fundamental Active Power, 1 second average
532 | 0x0214 | 2 | Float | 5 | Watt | R | Total Active Power, 1 second average
534 | 0x0216 | 2 | Float | 5 | Watt | R | Fundamental Active Power, 1 second average
536 | 0x0218 | 2 | Float | 6 | Watt | R | Total Active Power, 1 second average
538 | 0x021A | 2 | Float | 6 | Watt | R | Fundamental Active Power, 1 second average
540 | 0x021C | 2 | Float | 7 | Watt | R | Total Active Power, 1 second average
542 | 0x021E | 2 | Float | 7 | Watt | R | Fundamental Active Power, 1 second average
544 | 0x0220 | 2 | Float | 8 | Watt | R | Total Active Power, 1 second average
546 | 0x0222 | 2 | Float | 8 | Watt | R | Fundamental Active Power, 1 second average
548 | 0x0224 | 2 | Float | 9 | Watt | R | Total Active Power, 1 second average
550 | 0x0226 | 2 | Float | 9 | Watt | R | Fundamental Active Power, 1 second average
552 | 0x0228 | 2 | Float | 10 | Watt | R | Total Active Power, 1 second average
554 | 0x022A | 2 | Float | 10 | Watt | R | Fundamental Active Power, 1 second average
556 | 0x022C | 2 | Float | 11 | Watt | R | Total Active Power, 1 second average
558 | 0x022E | 2 | Float | 11 | Watt | R | Fundamental Active Power, 1 second average
560 | 0x0230 | 2 | Float | 12 | Watt | R | Total Active Power, 1 second average
562 | 0x0232 | 2 | Float | 12 | Watt | R | Fundamental Active Power, 1 second average
564 | 0x0234 | 2 | Float | 13 | Watt | R | Total Active Power, 1 second average
566 | 0x0236 | 2 | Float | 13 | Watt | R | Fundamental Active Power, 1 second average
640 | 0x0280 | 2 | Float | 0 | var | R | Total Reactive Power, 1 second average
642 | 0x0282 | 2 | Float | 0 | var | R | Fundamental Reactive Power, 1 second average
644 | 0x0284 | 2 | Float | 1 | var | R | Total Reactive Power, 1 second average
646 | 0x0286 | 2 | Float | 1 | var | R | Fundamental Reactive Power, 1 second average
648 | 0x0288 | 2 | Float | 2 | var | R | Total Reactive Power, 1 second average
650 | 0x028A | 2 | Float | 2 | var | R | Fundamental Reactive Power, 1 second average
652 | 0x028C | 2 | Float | 3 | var | R | Total Reactive Power, 1 second average
654 | 0x028E | 2 | Float | 3 | var | R | Fundamental Reactive Power, 1 second average
656 | 0x0290 | 2 | Float | 4 | var | R | Total Reactive Power, 1 second average
658 | 0x0292 | 2 | Float | 4 | var | R | Fundamental Reactive Power, 1 second average
660 | 0x0294 | 2 | Float | 5 | var | R | Total Reactive Power, 1 second average
662 | 0x0296 | 2 | Float | 5 | var | R | Fundamental Reactive Power, 1 second average
664 | 0x0298 | 2 | Float | 6 | var | R | Total Reactive Power, 1 second average
666 | 0x029A | 2 | Float | 6 | var | R | Fundamental Reactive Power, 1 second average
668 | 0x029C | 2 | Float | 7 | var | R | Total Reactive Power, 1 second average
670 | 0x029E | 2 | Float | 7 | var | R | Fundamental Reactive Power, 1 second average
672 | 0x02A0 | 2 | Float | 8 | var | R | Total Reactive Power, 1 second average
674 | 0x02A2 | 2 | Float | 8 | var | R | Fundamental Reactive Power, 1 second average
676 | 0x02A4 | 2 | Float | 9 | var | R | Total Reactive Power, 1 second average
678 | 0x02A6 | 2 | Float | 9 | var | R | Fundamental Reactive Power, 1 second average
680 | 0x02A8 | 2 | Float | 10 | var | R | Total Reactive Power, 1 second average
682 | 0x02AA | 2 | Float | 10 | var | R | Fundamental Reactive Power, 1 second average
684 | 0x02AC | 2 | Float | 11 | var | R | Total Reactive Power, 1 second average
686 | 0x02AE | 2 | Float | 11 | var | R | Fundamental Reactive Power, 1 second average
688 | 0x02B0 | 2 | Float | 12 | var | R | Total Reactive Power, 1 second average
690 | 0x02B2 | 2 | Float | 12 | var | R | Fundamental Reactive Power, 1 second average
692 | 0x02B4 | 2 | Float | 13 | var | R | Total Reactive Power, 1 second average
694 | 0x02B6 | 2 | Float | 13 | var | R | Fundamental Reactive Power, 1 second average
960 | 0x03C0 | 2 | Float | 0 | var | R | Total Instantaneous Active Power, 100 ms average
962 | 0x03C2 | 2 | Float | 1 | var | R | Total Instantaneous Active Power, 100 ms average
964 | 0x03C4 | 2 | Float | 2 | var | R | Total Instantaneous Active Power, 100 ms average
966 | 0x03C6 | 2 | Float | 3 | var | R | Total Instantaneous Active Power, 100 ms average
968 | 0x03C8 | 2 | Float | 4 | var | R | Total Instantaneous Active Power, 100 ms average
970 | 0x03CA | 2 | Float | 5 | var | R | Total Instantaneous Active Power, 100 ms average
972 | 0x03CC | 2 | Float | 6 | var | R | Total Instantaneous Active Power, 100 ms average
974 | 0x03CE | 2 | Float | 7 | var | R | Total Instantaneous Active Power, 100 ms average
976 | 0x03D0 | 2 | Float | 8 | var | R | Total Instantaneous Active Power, 100 ms average
978 | 0x03D2 | 2 | Float | 9 | var | R | Total Instantaneous Active Power, 100 ms average
980 | 0x03D4 | 2 | Float | 10 | Watt | R | Total Instantaneous Active Power, 100 ms average
982 | 0x03D6 | 2 | Float | 11 | Watt | R | Total Instantaneous Active Power, 100 ms average
984 | 0x03D8 | 2 | Float | 12 | Watt | R | Total Instantaneous Active Power, 100 ms average
986 | 0x03DA | 2 | Float | 13 | Watt | R | Total Instantaneous Active Power, 100 ms average

## Energy
Modbus Address | Modbus Address (Hex) | Size | Type | Channel | Unit | R/W | Description
12288 | 0x3000 | 2 | Int32 | 0 | Watthour | RW | Active Import
12290 | 0x3002 | 2 | Int32 | 0 | Watthour | RW | Active Export
12292 | 0x3004 | 2 | Int32 | 1 | Watthour | RW | Active Import
12294 | 0x3006 | 2 | Int32 | 1 | Watthour | RW | Active Export
12296 | 0x3008 | 2 | Int32 | 2 | Watthour | RW | Active Import
12298 | 0x300A | 2 | Int32 | 2 | Watthour | RW | Active Export
12300 | 0x300C | 2 | Int32 | 3 | Watthour | RW | Active Import
12302 | 0x300E | 2 | Int32 | 3 | Watthour | RW | Active Export
12304 | 0x3010 | 2 | Int32 | 4 | Watthour | RW | Active Import
12306 | 0x3012 | 2 | Int32 | 4 | Watthour | RW | Active Export
12308 | 0x3014 | 2 | Int32 | 5 | Watthour | RW | Active Import
12310 | 0x3016 | 2 | Int32 | 5 | Watthour | RW | Active Export
12312 | 0x3018 | 2 | Int32 | 6 | Watthour | RW | Active Import
12314 | 0x301A | 2 | Int32 | 6 | Watthour | RW | Active Export
12316 | 0x301C | 2 | Int32 | 7 | Watthour | RW | Active Import
12318 | 0x301E | 2 | Int32 | 7 | Watthour | RW | Active Export
12320 | 0x3020 | 2 | Int32 | 8 | Watthour | RW | Active Import
12322 | 0x3022 | 2 | Int32 | 8 | Watthour | RW | Active Export
12324 | 0x3024 | 2 | Int32 | 9 | Watthour | RW | Active Import
12326 | 0x3026 | 2 | Int32 | 9 | Watthour | RW | Active Export
12328 | 0x3028 | 2 | Int32 | 10 | Watthour | RW | Active Import
12330 | 0x302A | 2 | Int32 | 10 | Watthour | RW | Active Export
12332 | 0x302C | 2 | Int32 | 11 | Watthour | RW | Active Import
12334 | 0x302E | 2 | Int32 | 11 | Watthour | RW | Active Export
12336 | 0x3030 | 2 | Int32 | 12 | Watthour | RW | Active Import
12338 | 0x3032 | 2 | Int32 | 12 | Watthour | RW | Active Export
12340 | 0x3034 | 2 | Int32 | 13 | Watthour | RW | Active Import
12342 | 0x3036 | 2 | Int32 | 13 | Watthour | RW | Active Export
12344 | 0x3038 | 2 | Int32 | 14 | Watthour | RW | Active Import
12346 | 0x303A | 2 | Int32 | 14 | Watthour | RW | Active Export
12348 | 0x303C | 2 | Int32 | 15 | Watthour | RW | Active Import
12350 | 0x303E | 2 | Int32 | 15 | Watthour | RW | Active Export
12352 | 0x3040 | 2 | Int32 | 16 | Watthour | RW | Active Import
12354 | 0x3042 | 2 | Int32 | 16 | Watthour | RW | Active Export
12356 | 0x3044 | 2 | Int32 | 17 | Watthour | RW | Active Import
12358 | 0x3046 | 2 | Int32 | 17 | Watthour | RW | Active Export
12360 | 0x3048 | 2 | Int32 | 18 | Watthour | RW | Active Import
12362 | 0x304A | 2 | Int32 | 18 | Watthour | RW | Active Export
12364 | 0x304C | 2 | Int32 | 19 | Watthour | RW | Active Import
12366 | 0x304E | 2 | Int32 | 19 | Watthour | RW | Active Export
12368 | 0x3050 | 2 | Int32 | 20 | Watthour | RW | Active Import
12370 | 0x3052 | 2 | Int32 | 20 | Watthour | RW | Active Export
12372 | 0x3054 | 2 | Int32 | 21 | Watthour | RW | Active Import
12374 | 0x3056 | 2 | Int32 | 21 | Watthour | RW | Active Export
12376 | 0x3058 | 2 | Int32 | 22 | Watthour | RW | Active Import
12378 | 0x305A | 2 | Int32 | 22 | Watthour | RW | Active Export
12380 | 0x305C | 2 | Int32 | 23 | Watthour | RW | Active Import
12382 | 0x305E | 2 | Int32 | 23 | Watthour | RW | Active Export
12384 | 0x3060 | 2 | Int32 | 24 | Watthour | RW | Active Import
12386 | 0x3062 | 2 | Int32 | 24 | Watthour | RW | Active Export
12388 | 0x3064 | 2 | Int32 | 25 | Watthour | RW | Active Import
12390 | 0x3066 | 2 | Int32 | 25 | Watthour | RW | Active Export
12392 | 0x3068 | 2 | Int32 | 26 | Watthour | RW | Active Import
12394 | 0x306A | 2 | Int32 | 26 | Watthour | RW | Active Export
12396 | 0x306C | 2 | Int32 | 27 | Watthour | RW | Active Import
12398 | 0x306E | 2 | Int32 | 27 | Watthour | RW | Active Export
12416 | 0x3080 | 2 | Int32 | 0 | varh | RW | Reactive Import
12418 | 0x3082 | 2 | Int32 | 0 | varh | RW | Reactive Export
12420 | 0x3084 | 2 | Int32 | 1 | varh | RW | Reactive Import
12422 | 0x3086 | 2 | Int32 | 1 | varh | RW | Reactive Export
12424 | 0x3088 | 2 | Int32 | 2 | varh | RW | Reactive Import
12426 | 0x308A | 2 | Int32 | 2 | varh | RW | Reactive Export
12428 | 0x308C | 2 | Int32 | 3 | varh | RW | Reactive Import
12430 | 0x308E | 2 | Int32 | 3 | varh | RW | Reactive Export
12432 | 0x3090 | 2 | Int32 | 4 | varh | RW | Reactive Import
12434 | 0x3092 | 2 | Int32 | 4 | varh | RW | Reactive Export
12436 | 0x3094 | 2 | Int32 | 5 | varh | RW | Reactive Import
12438 | 0x3096 | 2 | Int32 | 5 | varh | RW | Reactive Export
12440 | 0x3098 | 2 | Int32 | 6 | varh | RW | Reactive Import
12442 | 0x309A | 2 | Int32 | 6 | varh | RW | Reactive Export
12444 | 0x309C | 2 | Int32 | 7 | varh | RW | Reactive Import
12446 | 0x309E | 2 | Int32 | 7 | varh | RW | Reactive Export
12448 | 0x30A0 | 2 | Int32 | 8 | varh | RW | Reactive Import
12450 | 0x30A2 | 2 | Int32 | 8 | varh | RW | Reactive Export
12452 | 0x30A4 | 2 | Int32 | 9 | varh | RW | Reactive Import
12454 | 0x30A6 | 2 | Int32 | 9 | varh | RW | Reactive Export
12456 | 0x30A8 | 2 | Int32 | 10 | varh | RW | Reactive Import
12458 | 0x30AA | 2 | Int32 | 10 | varh | RW | Reactive Export
12460 | 0x30AC | 2 | Int32 | 11 | varh | RW | Reactive Import
12462 | 0x30AE | 2 | Int32 | 11 | varh | RW | Reactive Export
12464 | 0x30B0 | 2 | Int32 | 12 | varh | RW | Reactive Import
12466 | 0x30B2 | 2 | Int32 | 12 | varh | RW | Reactive Export
12468 | 0x30B4 | 2 | Int32 | 13 | varh | RW | Reactive Import
12470 | 0x30B6 | 2 | Int32 | 13 | varh | RW | Reactive Export
12472 | 0x30B8 | 2 | Int32 | 14 | varh | RW | Reactive Import
12474 | 0x30BA | 2 | Int32 | 14 | varh | RW | Reactive Export
12476 | 0x30BC | 2 | Int32 | 15 | varh | RW | Reactive Import
12478 | 0x30BE | 2 | Int32 | 15 | varh | RW | Reactive Export
12480 | 0x30C0 | 2 | Int32 | 16 | varh | RW | Reactive Import
12482 | 0x30C2 | 2 | Int32 | 16 | varh | RW | Reactive Export
12484 | 0x30C4 | 2 | Int32 | 17 | varh | RW | Reactive Import
12486 | 0x30C6 | 2 | Int32 | 17 | varh | RW | Reactive Export
12488 | 0x30C8 | 2 | Int32 | 18 | varh | RW | Reactive Import
12490 | 0x30CA | 2 | Int32 | 18 | varh | RW | Reactive Export
12492 | 0x30CC | 2 | Int32 | 19 | varh | RW | Reactive Import
12494 | 0x30CE | 2 | Int32 | 19 | varh | RW | Reactive Export
12496 | 0x30D0 | 2 | Int32 | 20 | varh | RW | Reactive Import
12498 | 0x30D2 | 2 | Int32 | 20 | varh | RW | Reactive Export
12500 | 0x30D4 | 2 | Int32 | 21 | varh | RW | Reactive Import
12502 | 0x30D6 | 2 | Int32 | 21 | varh | RW | Reactive Export
12504 | 0x30D8 | 2 | Int32 | 22 | varh | RW | Reactive Import
12506 | 0x30DA | 2 | Int32 | 22 | varh | RW | Reactive Export
12508 | 0x30DC | 2 | Int32 | 23 | varh | RW | Reactive Import
12510 | 0x30DE | 2 | Int32 | 23 | varh | RW | Reactive Export
12512 | 0x30E0 | 2 | Int32 | 24 | varh | RW | Reactive Import
12514 | 0x30E2 | 2 | Int32 | 24 | varh | RW | Reactive Export
12516 | 0x30E4 | 2 | Int32 | 25 | varh | RW | Reactive Import
12518 | 0x30E6 | 2 | Int32 | 25 | varh | RW | Reactive Export
12520 | 0x30E8 | 2 | Int32 | 26 | varh | RW | Reactive Import
12522 | 0x30EA | 2 | Int32 | 26 | varh | RW | Reactive Export
12524 | 0x30EC | 2 | Int32 | 27 | varh | RW | Reactive Import
12526 | 0x30EE | 2 | Int32 | 27 | varh | RW | Reactive Export

## Virtual Channel Energy
Modbus Address | Modbus Address (Hex) | Size | Type | Virtual channel | Unit | R/W | Description
12544 | 0x3100 | 2 | Int32 | 0 | Watthour | RW | Active Import
12546 | 0x3102 | 2 | Int32 | 0 | Watthour | RW | Active Export
12548 | 0x3104 | 2 | Int32 | 0 | varh | RW | Reactive Import
12550 | 0x3106 | 2 | Int32 | 0 | varh | RW | Reactive Export
12552 | 0x3108 | 2 | Int32 | 1 | Watthour | RW | Active Import
12554 | 0x310A | 2 | Int32 | 1 | Watthour | RW | Active Export
12556 | 0x310C | 2 | Int32 | 1 | varh | RW | Reactive Import
12558 | 0x310E | 2 | Int32 | 1 | varh | RW | Reactive Export
12560 | 0x3110 | 2 | Int32 | 2 | Watthour | RW | Active Import
12562 | 0x3112 | 2 | Int32 | 2 | Watthour | RW | Active Export
12564 | 0x3114 | 2 | Int32 | 2 | varh | RW | Reactive Import
12566 | 0x3116 | 2 | Int32 | 2 | varh | RW | Reactive Export
12568 | 0x3118 | 2 | Int32 | 3 | Watthour | RW | Active Import
12570 | 0x311A | 2 | Int32 | 3 | Watthour | RW | Active Export
12572 | 0x311C | 2 | Int32 | 3 | varh | RW | Reactive Import
12574 | 0x311E | 2 | Int32 | 3 | varh | RW | Reactive Export
12576 | 0x3120 | 2 | Int32 | 4 | Watthour | RW | Active Import
12578 | 0x3122 | 2 | Int32 | 4 | Watthour | RW | Active Export
12580 | 0x3124 | 2 | Int32 | 4 | varh | RW | Reactive Import
12582 | 0x3126 | 2 | Int32 | 4 | varh | RW | Reactive Export
12584 | 0x3128 | 2 | Int32 | 5 | Watthour | RW | Active Import
12586 | 0x312A | 2 | Int32 | 5 | Watthour | RW | Active Export
12588 | 0x312C | 2 | Int32 | 5 | varh | RW | Reactive Import
12590 | 0x312E | 2 | Int32 | 5 | varh | RW | Reactive Export
12592 | 0x3130 | 2 | Int32 | 6 | Watthour | RW | Active Import
12594 | 0x3132 | 2 | Int32 | 6 | Watthour | RW | Active Export
12596 | 0x3134 | 2 | Int32 | 6 | varh | RW | Reactive Import
12598 | 0x3136 | 2 | Int32 | 6 | varh | RW | Reactive Export
12600 | 0x3138 | 2 | Int32 | 7 | Watthour | RW | Active Import
12602 | 0x313A | 2 | Int32 | 7 | Watthour | RW | Active Export
12604 | 0x313C | 2 | Int32 | 7 | varh | RW | Reactive Import
12606 | 0x313E | 2 | Int32 | 7 | varh | RW | Reactive Export
12608 | 0x3140 | 2 | Int32 | 8 | Watthour | RW | Active Import
12610 | 0x3142 | 2 | Int32 | 8 | Watthour | RW | Active Export
12612 | 0x3144 | 2 | Int32 | 8 | varh | RW | Reactive Import
12614 | 0x3146 | 2 | Int32 | 8 | varh | RW | Reactive Export
12616 | 0x3148 | 2 | Int32 | 9 | Watthour | RW | Active Import
12618 | 0x314A | 2 | Int32 | 9 | Watthour | RW | Active Export
12620 | 0x314C | 2 | Int32 | 9 | varh | RW | Reactive Import
12622 | 0x314E | 2 | Int32 | 9 | varh | RW | Reactive Export
12624 | 0x3150 | 2 | Int32 | 10 | Watthour | RW | Active Import
12626 | 0x3152 | 2 | Int32 | 10 | Watthour | RW | Active Export
12628 | 0x3154 | 2 | Int32 | 10 | varh | RW | Reactive Import
12630 | 0x3156 | 2 | Int32 | 10 | varh | RW | Reactive Export
12632 | 0x3158 | 2 | Int32 | 11 | Watthour | RW | Active Import
12634 | 0x315A | 2 | Int32 | 11 | Watthour | RW | Active Export
12636 | 0x315C | 2 | Int32 | 11 | varh | RW | Reactive Import
12638 | 0x315E | 2 | Int32 | 11 | varh | RW | Reactive Export
12640 | 0x3160 | 2 | Int32 | 12 | Watthour | RW | Active Import
12642 | 0x3162 | 2 | Int32 | 12 | Watthour | RW | Active Export
12644 | 0x3164 | 2 | Int32 | 12 | varh | RW | Reactive Import
12646 | 0x3166 | 2 | Int32 | 12 | varh | RW | Reactive Export
12648 | 0x3168 | 2 | Int32 | 13 | Watthour | RW | Active Import
12650 | 0x316A | 2 | Int32 | 13 | Watthour | RW | Active Export
12652 | 0x316C | 2 | Int32 | 13 | varh | RW | Reactive Import
12654 | 0x316E | 2 | Int32 | 13 | varh | RW | Reactive Export

## Frequency
Modbus Address | Modbus Address (Hex) | Size | Type | Unit | R/W | Description
1014 | 0x03F6 | 2 | Float | Hertz | R | Nominal Frequency, 50 or 60 Hz
1016 | 0x03F8 | 2 | Float | Hertz | R | Actual Frequency, 200 ms average
1018 | 0x03FA | 2 | Int32 | seconds | R | Run time in seconds, when this value changes, new 1 second data is available

## Events (hidden)
Modbus Address | Modbus Address (Hex) | Size | Type | Channel | Unit | R/W | Description
1020 | 0x03FC | 2 | Int32 |  |  | R | Total Event count
1022 | 0x03FE | 1 | Int16 |  |  | R | Event mask, reading this value resets the mask
1024 | 0x0400 | 2 | Float | 0 | µs | R | Event duration
1026 | 0x0402 | 2 | Float | 0 | Watt | R | Event Maximum Active Power
1028 | 0x0404 | 2 | Float | 0 | Watt | R | Event Delta Active Power
1030 | 0x0406 | 2 | Float | 0 | var | R | Event Delta Reactive Power
1032 | 0x0408 | 2 | Float | 0 | Watt | R | Event End Active Power
1034 | 0x040A | 2 | Float | 0 | var | R | Event End Reactive Power
1036 | 0x040C | 2 | Float | 0 | VA | R | Event Delta Power for Harmonic 1
1038 | 0x040E | 2 | Float | 0 | VA | R | Event Delta Power for Harmonic 2
1040 | 0x0410 | 2 | Float | 0 | VA | R | Event Delta Power for Harmonic 3
1042 | 0x0412 | 2 | Float | 0 | VA | R | Event Delta Power for Harmonic 4
1044 | 0x0414 | 2 | Float | 0 | VA | R | Event Delta Power for Harmonic 5
1046 | 0x0416 | 2 | Float | 0 | VA | R | Event Delta Power for Harmonic 6
1048 | 0x0418 | 2 | Float | 0 | VA | R | Event Delta Power for Harmonic 7
1050 | 0x041A | 2 | Float | 0 | VA | R | Event Delta Power for Harmonic 8
1052 | 0x041C | 2 | Float | 0 | VA | R | Event Delta Power for Harmonic 9
1054 | 0x041E | 2 | Float | 0 | VA | R | Event Delta Power for Harmonic 10
1056 | 0x0420 | 2 | Float | 0 | VA | R | Event Delta Power for Harmonic 11
1058 | 0x0422 | 2 | Float | 0 | VA | R | Event Delta Power for Harmonic 13
1060 | 0x0424 | 2 | Float | 0 | VA | R | Event Delta Power for Harmonic 15
1062 | 0x0426 | 2 | Float | 0 | VA | R | Event Delta Power for Harmonic 17
1064 | 0x0428 | 2 | Float | 0 | VA | R | Event Delta Power for Harmonic 19
1066 | 0x042A | 2 | Int32 | 0 | VA | R | Event count
1152 | 0x0480 | 2 | Float | 1 | µs | R | Event duration
1154 | 0x0482 | 2 | Float | 1 | Watt | R | Event Maximum Active Power
1156 | 0x0484 | 2 | Float | 1 | Watt | R | Event Delta Active Power
1158 | 0x0486 | 2 | Float | 1 | var | R | Event Delta Reactive Power
1160 | 0x0488 | 2 | Float | 1 | Watt | R | Event End Active Power
1162 | 0x048A | 2 | Float | 1 | var | R | Event End Reactive Power
1164 | 0x048C | 2 | Float | 1 | VA | R | Event Delta Power for Harmonic 1
1166 | 0x048E | 2 | Float | 1 | VA | R | Event Delta Power for Harmonic 2
1168 | 0x0490 | 2 | Float | 1 | VA | R | Event Delta Power for Harmonic 3
1170 | 0x0492 | 2 | Float | 1 | VA | R | Event Delta Power for Harmonic 4
1172 | 0x0494 | 2 | Float | 1 | VA | R | Event Delta Power for Harmonic 5
1174 | 0x0496 | 2 | Float | 1 | VA | R | Event Delta Power for Harmonic 6
1176 | 0x0498 | 2 | Float | 1 | VA | R | Event Delta Power for Harmonic 7
1178 | 0x049A | 2 | Float | 1 | VA | R | Event Delta Power for Harmonic 8
1180 | 0x049C | 2 | Float | 1 | VA | R | Event Delta Power for Harmonic 9
1182 | 0x049E | 2 | Float | 1 | VA | R | Event Delta Power for Harmonic 10
1184 | 0x04A0 | 2 | Float | 1 | VA | R | Event Delta Power for Harmonic 11
1186 | 0x04A2 | 2 | Float | 1 | VA | R | Event Delta Power for Harmonic 13
1188 | 0x04A4 | 2 | Float | 1 | VA | R | Event Delta Power for Harmonic 15
1190 | 0x04A6 | 2 | Float | 1 | VA | R | Event Delta Power for Harmonic 17
1192 | 0x04A8 | 2 | Float | 1 | VA | R | Event Delta Power for Harmonic 19
1194 | 0x04AA | 2 | Int32 | 1 | VA | R | Event count
1280 | 0x0500 | 2 | Float | 2 | µs | R | Event duration
1282 | 0x0502 | 2 | Float | 2 | Watt | R | Event Maximum Active Power
1284 | 0x0504 | 2 | Float | 2 | Watt | R | Event Delta Active Power
1286 | 0x0506 | 2 | Float | 2 | var | R | Event Delta Reactive Power
1288 | 0x0508 | 2 | Float | 2 | Watt | R | Event End Active Power
1290 | 0x050A | 2 | Float | 2 | var | R | Event End Reactive Power
1292 | 0x050C | 2 | Float | 2 | VA | R | Event Delta Power for Harmonic 1
1294 | 0x050E | 2 | Float | 2 | VA | R | Event Delta Power for Harmonic 2
1296 | 0x0510 | 2 | Float | 2 | VA | R | Event Delta Power for Harmonic 3
1298 | 0x0512 | 2 | Float | 2 | VA | R | Event Delta Power for Harmonic 4
1300 | 0x0514 | 2 | Float | 2 | VA | R | Event Delta Power for Harmonic 5
1302 | 0x0516 | 2 | Float | 2 | VA | R | Event Delta Power for Harmonic 6
1304 | 0x0518 | 2 | Float | 2 | VA | R | Event Delta Power for Harmonic 7
1306 | 0x051A | 2 | Float | 2 | VA | R | Event Delta Power for Harmonic 8
1308 | 0x051C | 2 | Float | 2 | VA | R | Event Delta Power for Harmonic 9
1310 | 0x051E | 2 | Float | 2 | VA | R | Event Delta Power for Harmonic 10
1312 | 0x0520 | 2 | Float | 2 | VA | R | Event Delta Power for Harmonic 11
1314 | 0x0522 | 2 | Float | 2 | VA | R | Event Delta Power for Harmonic 13
1316 | 0x0524 | 2 | Float | 2 | VA | R | Event Delta Power for Harmonic 15
1318 | 0x0526 | 2 | Float | 2 | VA | R | Event Delta Power for Harmonic 17
1320 | 0x0528 | 2 | Float | 2 | VA | R | Event Delta Power for Harmonic 19
1322 | 0x052A | 2 | Int32 | 2 | VA | R | Event count
1408 | 0x0580 | 2 | Float | 3 | µs | R | Event duration
1410 | 0x0582 | 2 | Float | 3 | Watt | R | Event Maximum Active Power
1412 | 0x0584 | 2 | Float | 3 | Watt | R | Event Delta Active Power
1414 | 0x0586 | 2 | Float | 3 | var | R | Event Delta Reactive Power
1416 | 0x0588 | 2 | Float | 3 | Watt | R | Event End Active Power
1418 | 0x058A | 2 | Float | 3 | var | R | Event End Reactive Power
1420 | 0x058C | 2 | Float | 3 | VA | R | Event Delta Power for Harmonic 1
1422 | 0x058E | 2 | Float | 3 | VA | R | Event Delta Power for Harmonic 2
1424 | 0x0590 | 2 | Float | 3 | VA | R | Event Delta Power for Harmonic 3
1426 | 0x0592 | 2 | Float | 3 | VA | R | Event Delta Power for Harmonic 4
1428 | 0x0594 | 2 | Float | 3 | VA | R | Event Delta Power for Harmonic 5
1430 | 0x0596 | 2 | Float | 3 | VA | R | Event Delta Power for Harmonic 6
1432 | 0x0598 | 2 | Float | 3 | VA | R | Event Delta Power for Harmonic 7
1434 | 0x059A | 2 | Float | 3 | VA | R | Event Delta Power for Harmonic 8
1436 | 0x059C | 2 | Float | 3 | VA | R | Event Delta Power for Harmonic 9
1438 | 0x059E | 2 | Float | 3 | VA | R | Event Delta Power for Harmonic 10
1440 | 0x05A0 | 2 | Float | 3 | VA | R | Event Delta Power for Harmonic 11
1442 | 0x05A2 | 2 | Float | 3 | VA | R | Event Delta Power for Harmonic 13
1444 | 0x05A4 | 2 | Float | 3 | VA | R | Event Delta Power for Harmonic 15
1446 | 0x05A6 | 2 | Float | 3 | VA | R | Event Delta Power for Harmonic 17
1448 | 0x05A8 | 2 | Float | 3 | VA | R | Event Delta Power for Harmonic 19
1450 | 0x05AA | 2 | Int32 | 3 | VA | R | Event count
1536 | 0x0600 | 2 | Float | 4 | µs | R | Event duration
1538 | 0x0602 | 2 | Float | 4 | Watt | R | Event Maximum Active Power
1540 | 0x0604 | 2 | Float | 4 | Watt | R | Event Delta Active Power
1542 | 0x0606 | 2 | Float | 4 | var | R | Event Delta Reactive Power
1544 | 0x0608 | 2 | Float | 4 | Watt | R | Event End Active Power
1546 | 0x060A | 2 | Float | 4 | var | R | Event End Reactive Power
1548 | 0x060C | 2 | Float | 4 | VA | R | Event Delta Power for Harmonic 1
1550 | 0x060E | 2 | Float | 4 | VA | R | Event Delta Power for Harmonic 2
1552 | 0x0610 | 2 | Float | 4 | VA | R | Event Delta Power for Harmonic 3
1554 | 0x0612 | 2 | Float | 4 | VA | R | Event Delta Power for Harmonic 4
1556 | 0x0614 | 2 | Float | 4 | VA | R | Event Delta Power for Harmonic 5
1558 | 0x0616 | 2 | Float | 4 | VA | R | Event Delta Power for Harmonic 6
1560 | 0x0618 | 2 | Float | 4 | VA | R | Event Delta Power for Harmonic 7
1562 | 0x061A | 2 | Float | 4 | VA | R | Event Delta Power for Harmonic 8
1564 | 0x061C | 2 | Float | 4 | VA | R | Event Delta Power for Harmonic 9
1566 | 0x061E | 2 | Float | 4 | VA | R | Event Delta Power for Harmonic 10
1568 | 0x0620 | 2 | Float | 4 | VA | R | Event Delta Power for Harmonic 11
1570 | 0x0622 | 2 | Float | 4 | VA | R | Event Delta Power for Harmonic 13
1572 | 0x0624 | 2 | Float | 4 | VA | R | Event Delta Power for Harmonic 15
1574 | 0x0626 | 2 | Float | 4 | VA | R | Event Delta Power for Harmonic 17
1576 | 0x0628 | 2 | Float | 4 | VA | R | Event Delta Power for Harmonic 19
1578 | 0x062A | 2 | Int32 | 4 | VA | R | Event count
1664 | 0x0680 | 2 | Float | 5 | µs | R | Event duration
1666 | 0x0682 | 2 | Float | 5 | Watt | R | Event Maximum Active Power
1668 | 0x0684 | 2 | Float | 5 | Watt | R | Event Delta Active Power
1670 | 0x0686 | 2 | Float | 5 | var | R | Event Delta Reactive Power
1672 | 0x0688 | 2 | Float | 5 | Watt | R | Event End Active Power
1674 | 0x068A | 2 | Float | 5 | var | R | Event End Reactive Power
1676 | 0x068C | 2 | Float | 5 | VA | R | Event Delta Power for Harmonic 1
1678 | 0x068E | 2 | Float | 5 | VA | R | Event Delta Power for Harmonic 2
1680 | 0x0690 | 2 | Float | 5 | VA | R | Event Delta Power for Harmonic 3
1682 | 0x0692 | 2 | Float | 5 | VA | R | Event Delta Power for Harmonic 4
1684 | 0x0694 | 2 | Float | 5 | VA | R | Event Delta Power for Harmonic 5
1686 | 0x0696 | 2 | Float | 5 | VA | R | Event Delta Power for Harmonic 6
1688 | 0x0698 | 2 | Float | 5 | VA | R | Event Delta Power for Harmonic 7
1690 | 0x069A | 2 | Float | 5 | VA | R | Event Delta Power for Harmonic 8
1692 | 0x069C | 2 | Float | 5 | VA | R | Event Delta Power for Harmonic 9
1694 | 0x069E | 2 | Float | 5 | VA | R | Event Delta Power for Harmonic 10
1696 | 0x06A0 | 2 | Float | 5 | VA | R | Event Delta Power for Harmonic 11
1698 | 0x06A2 | 2 | Float | 5 | VA | R | Event Delta Power for Harmonic 13
1700 | 0x06A4 | 2 | Float | 5 | VA | R | Event Delta Power for Harmonic 15
1702 | 0x06A6 | 2 | Float | 5 | VA | R | Event Delta Power for Harmonic 17
1704 | 0x06A8 | 2 | Float | 5 | VA | R | Event Delta Power for Harmonic 19
1706 | 0x06AA | 2 | Int32 | 5 | VA | R | Event count
1792 | 0x0700 | 2 | Float | 6 | µs | R | Event duration
1794 | 0x0702 | 2 | Float | 6 | Watt | R | Event Maximum Active Power
1796 | 0x0704 | 2 | Float | 6 | Watt | R | Event Delta Active Power
1798 | 0x0706 | 2 | Float | 6 | var | R | Event Delta Reactive Power
1800 | 0x0708 | 2 | Float | 6 | Watt | R | Event End Active Power
1802 | 0x070A | 2 | Float | 6 | var | R | Event End Reactive Power
1804 | 0x070C | 2 | Float | 6 | VA | R | Event Delta Power for Harmonic 1
1806 | 0x070E | 2 | Float | 6 | VA | R | Event Delta Power for Harmonic 2
1808 | 0x0710 | 2 | Float | 6 | VA | R | Event Delta Power for Harmonic 3
1810 | 0x0712 | 2 | Float | 6 | VA | R | Event Delta Power for Harmonic 4
1812 | 0x0714 | 2 | Float | 6 | VA | R | Event Delta Power for Harmonic 5
1814 | 0x0716 | 2 | Float | 6 | VA | R | Event Delta Power for Harmonic 6
1816 | 0x0718 | 2 | Float | 6 | VA | R | Event Delta Power for Harmonic 7
1818 | 0x071A | 2 | Float | 6 | VA | R | Event Delta Power for Harmonic 8
1820 | 0x071C | 2 | Float | 6 | VA | R | Event Delta Power for Harmonic 9
1822 | 0x071E | 2 | Float | 6 | VA | R | Event Delta Power for Harmonic 10
1824 | 0x0720 | 2 | Float | 6 | VA | R | Event Delta Power for Harmonic 11
1826 | 0x0722 | 2 | Float | 6 | VA | R | Event Delta Power for Harmonic 13
1828 | 0x0724 | 2 | Float | 6 | VA | R | Event Delta Power for Harmonic 15
1830 | 0x0726 | 2 | Float | 6 | VA | R | Event Delta Power for Harmonic 17
1832 | 0x0728 | 2 | Float | 6 | VA | R | Event Delta Power for Harmonic 19
1834 | 0x072A | 2 | Int32 | 6 | VA | R | Event count
1920 | 0x0780 | 2 | Float | 7 | µs | R | Event duration
1922 | 0x0782 | 2 | Float | 7 | Watt | R | Event Maximum Active Power
1924 | 0x0784 | 2 | Float | 7 | Watt | R | Event Delta Active Power
1926 | 0x0786 | 2 | Float | 7 | var | R | Event Delta Reactive Power
1928 | 0x0788 | 2 | Float | 7 | Watt | R | Event End Active Power
1930 | 0x078A | 2 | Float | 7 | var | R | Event End Reactive Power
1932 | 0x078C | 2 | Float | 7 | VA | R | Event Delta Power for Harmonic 1
1934 | 0x078E | 2 | Float | 7 | VA | R | Event Delta Power for Harmonic 2
1936 | 0x0790 | 2 | Float | 7 | VA | R | Event Delta Power for Harmonic 3
1938 | 0x0792 | 2 | Float | 7 | VA | R | Event Delta Power for Harmonic 4
1940 | 0x0794 | 2 | Float | 7 | VA | R | Event Delta Power for Harmonic 5
1942 | 0x0796 | 2 | Float | 7 | VA | R | Event Delta Power for Harmonic 6
1944 | 0x0798 | 2 | Float | 7 | VA | R | Event Delta Power for Harmonic 7
1946 | 0x079A | 2 | Float | 7 | VA | R | Event Delta Power for Harmonic 8
1948 | 0x079C | 2 | Float | 7 | VA | R | Event Delta Power for Harmonic 9
1950 | 0x079E | 2 | Float | 7 | VA | R | Event Delta Power for Harmonic 10
1952 | 0x07A0 | 2 | Float | 7 | VA | R | Event Delta Power for Harmonic 11
1954 | 0x07A2 | 2 | Float | 7 | VA | R | Event Delta Power for Harmonic 13
1956 | 0x07A4 | 2 | Float | 7 | VA | R | Event Delta Power for Harmonic 15
1958 | 0x07A6 | 2 | Float | 7 | VA | R | Event Delta Power for Harmonic 17
1960 | 0x07A8 | 2 | Float | 7 | VA | R | Event Delta Power for Harmonic 19
1962 | 0x07AA | 2 | Int32 | 7 | VA | R | Event count
2048 | 0x0800 | 2 | Float | 8 | µs | R | Event duration
2050 | 0x0802 | 2 | Float | 8 | Watt | R | Event Maximum Active Power
2052 | 0x0804 | 2 | Float | 8 | Watt | R | Event Delta Active Power
2054 | 0x0806 | 2 | Float | 8 | var | R | Event Delta Reactive Power
2056 | 0x0808 | 2 | Float | 8 | Watt | R | Event End Active Power
2058 | 0x080A | 2 | Float | 8 | var | R | Event End Reactive Power
2060 | 0x080C | 2 | Float | 8 | VA | R | Event Delta Power for Harmonic 1
2062 | 0x080E | 2 | Float | 8 | VA | R | Event Delta Power for Harmonic 2
2064 | 0x0810 | 2 | Float | 8 | VA | R | Event Delta Power for Harmonic 3
2066 | 0x0812 | 2 | Float | 8 | VA | R | Event Delta Power for Harmonic 4
2068 | 0x0814 | 2 | Float | 8 | VA | R | Event Delta Power for Harmonic 5
2070 | 0x0816 | 2 | Float | 8 | VA | R | Event Delta Power for Harmonic 6
2072 | 0x0818 | 2 | Float | 8 | VA | R | Event Delta Power for Harmonic 7
2074 | 0x081A | 2 | Float | 8 | VA | R | Event Delta Power for Harmonic 8
2076 | 0x081C | 2 | Float | 8 | VA | R | Event Delta Power for Harmonic 9
2078 | 0x081E | 2 | Float | 8 | VA | R | Event Delta Power for Harmonic 10
2080 | 0x0820 | 2 | Float | 8 | VA | R | Event Delta Power for Harmonic 11
2082 | 0x0822 | 2 | Float | 8 | VA | R | Event Delta Power for Harmonic 13
2084 | 0x0824 | 2 | Float | 8 | VA | R | Event Delta Power for Harmonic 15
2086 | 0x0826 | 2 | Float | 8 | VA | R | Event Delta Power for Harmonic 17
2088 | 0x0828 | 2 | Float | 8 | VA | R | Event Delta Power for Harmonic 19
2090 | 0x082A | 2 | Int32 | 8 | VA | R | Event count
2176 | 0x0880 | 2 | Float | 9 | µs | R | Event duration
2178 | 0x0882 | 2 | Float | 9 | Watt | R | Event Maximum Active Power
2180 | 0x0884 | 2 | Float | 9 | Watt | R | Event Delta Active Power
2182 | 0x0886 | 2 | Float | 9 | var | R | Event Delta Reactive Power
2184 | 0x0888 | 2 | Float | 9 | Watt | R | Event End Active Power
2186 | 0x088A | 2 | Float | 9 | var | R | Event End Reactive Power
2188 | 0x088C | 2 | Float | 9 | VA | R | Event Delta Power for Harmonic 1
2190 | 0x088E | 2 | Float | 9 | VA | R | Event Delta Power for Harmonic 2
2192 | 0x0890 | 2 | Float | 9 | VA | R | Event Delta Power for Harmonic 3
2194 | 0x0892 | 2 | Float | 9 | VA | R | Event Delta Power for Harmonic 4
2196 | 0x0894 | 2 | Float | 9 | VA | R | Event Delta Power for Harmonic 5
2198 | 0x0896 | 2 | Float | 9 | VA | R | Event Delta Power for Harmonic 6
2200 | 0x0898 | 2 | Float | 9 | VA | R | Event Delta Power for Harmonic 7
2202 | 0x089A | 2 | Float | 9 | VA | R | Event Delta Power for Harmonic 8
2204 | 0x089C | 2 | Float | 9 | VA | R | Event Delta Power for Harmonic 9
2206 | 0x089E | 2 | Float | 9 | VA | R | Event Delta Power for Harmonic 10
2208 | 0x08A0 | 2 | Float | 9 | VA | R | Event Delta Power for Harmonic 11
2210 | 0x08A2 | 2 | Float | 9 | VA | R | Event Delta Power for Harmonic 13
2212 | 0x08A4 | 2 | Float | 9 | VA | R | Event Delta Power for Harmonic 15
2214 | 0x08A6 | 2 | Float | 9 | VA | R | Event Delta Power for Harmonic 17
2216 | 0x08A8 | 2 | Float | 9 | VA | R | Event Delta Power for Harmonic 19
2218 | 0x08AA | 2 | Int32 | 9 | VA | R | Event count

## Harmonics
Modbus Address | Modbus Address (Hex) | Size | Type | Phase/Channel | Unit | R/W | Description
8192 | 0x2000 | 4 | Complex | L1-N | Volt | R | Harmonic 1
8196 | 0x2004 | 4 | Complex | L1-N | Volt | R | Harmonic 2
8200 | 0x2008 | 4 | Complex | L1-N | Volt | R | Harmonic 3
8204 | 0x200C | 4 | Complex | L1-N | Volt | R | Harmonic 4
8208 | 0x2010 | 4 | Complex | L1-N | Volt | R | Harmonic 5
8212 | 0x2014 | 4 | Complex | L1-N | Volt | R | Harmonic 6
8216 | 0x2018 | 4 | Complex | L1-N | Volt | R | Harmonic 7
8220 | 0x201C | 4 | Complex | L1-N | Volt | R | Harmonic 8
8224 | 0x2020 | 4 | Complex | L1-N | Volt | R | Harmonic 9
8228 | 0x2024 | 4 | Complex | L1-N | Volt | R | Harmonic 10
8232 | 0x2028 | 4 | Complex | L1-N | Volt | R | Harmonic 11
8236 | 0x202C | 4 | Complex | L1-N | Volt | R | Harmonic 13
8240 | 0x2030 | 4 | Complex | L1-N | Volt | R | Harmonic 15
8244 | 0x2034 | 4 | Complex | L1-N | Volt | R | Harmonic 17
8248 | 0x2038 | 4 | Complex | L1-N | Volt | R | Harmonic 19
8256 | 0x2040 | 4 | Complex | L2-N | Volt | R | Harmonic 1
8260 | 0x2044 | 4 | Complex | L2-N | Volt | R | Harmonic 2
8264 | 0x2048 | 4 | Complex | L2-N | Volt | R | Harmonic 3
8268 | 0x204C | 4 | Complex | L2-N | Volt | R | Harmonic 4
8272 | 0x2050 | 4 | Complex | L2-N | Volt | R | Harmonic 5
8276 | 0x2054 | 4 | Complex | L2-N | Volt | R | Harmonic 6
8280 | 0x2058 | 4 | Complex | L2-N | Volt | R | Harmonic 7
8284 | 0x205C | 4 | Complex | L2-N | Volt | R | Harmonic 8
8288 | 0x2060 | 4 | Complex | L2-N | Volt | R | Harmonic 9
8292 | 0x2064 | 4 | Complex | L2-N | Volt | R | Harmonic 10
8296 | 0x2068 | 4 | Complex | L2-N | Volt | R | Harmonic 11
8300 | 0x206C | 4 | Complex | L2-N | Volt | R | Harmonic 13
8304 | 0x2070 | 4 | Complex | L2-N | Volt | R | Harmonic 15
8308 | 0x2074 | 4 | Complex | L2-N | Volt | R | Harmonic 17
8312 | 0x2078 | 4 | Complex | L2-N | Volt | R | Harmonic 19
8320 | 0x2080 | 4 | Complex | L3-N | Volt | R | Harmonic 1
8324 | 0x2084 | 4 | Complex | L3-N | Volt | R | Harmonic 2
8328 | 0x2088 | 4 | Complex | L3-N | Volt | R | Harmonic 3
8332 | 0x208C | 4 | Complex | L3-N | Volt | R | Harmonic 4
8336 | 0x2090 | 4 | Complex | L3-N | Volt | R | Harmonic 5
8340 | 0x2094 | 4 | Complex | L3-N | Volt | R | Harmonic 6
8344 | 0x2098 | 4 | Complex | L3-N | Volt | R | Harmonic 7
8348 | 0x209C | 4 | Complex | L3-N | Volt | R | Harmonic 8
8352 | 0x20A0 | 4 | Complex | L3-N | Volt | R | Harmonic 9
8356 | 0x20A4 | 4 | Complex | L3-N | Volt | R | Harmonic 10
8360 | 0x20A8 | 4 | Complex | L3-N | Volt | R | Harmonic 11
8364 | 0x20AC | 4 | Complex | L3-N | Volt | R | Harmonic 13
8368 | 0x20B0 | 4 | Complex | L3-N | Volt | R | Harmonic 15
8372 | 0x20B4 | 4 | Complex | L3-N | Volt | R | Harmonic 17
8376 | 0x20B8 | 4 | Complex | L3-N | Volt | R | Harmonic 19
8448 | 0x2100 | 4 | Complex | 0 | Ampere | R | Harmonic 1
8452 | 0x2104 | 4 | Complex | 0 | Ampere | R | Harmonic 2
8456 | 0x2108 | 4 | Complex | 0 | Ampere | R | Harmonic 3
8460 | 0x210C | 4 | Complex | 0 | Ampere | R | Harmonic 4
8464 | 0x2110 | 4 | Complex | 0 | Ampere | R | Harmonic 5
8468 | 0x2114 | 4 | Complex | 0 | Ampere | R | Harmonic 6
8472 | 0x2118 | 4 | Complex | 0 | Ampere | R | Harmonic 7
8476 | 0x211C | 4 | Complex | 0 | Ampere | R | Harmonic 8
8480 | 0x2120 | 4 | Complex | 0 | Ampere | R | Harmonic 9
8484 | 0x2124 | 4 | Complex | 0 | Ampere | R | Harmonic 10
8488 | 0x2128 | 4 | Complex | 0 | Ampere | R | Harmonic 11
8492 | 0x212C | 4 | Complex | 0 | Ampere | R | Harmonic 13
8496 | 0x2130 | 4 | Complex | 0 | Ampere | R | Harmonic 15
8500 | 0x2134 | 4 | Complex | 0 | Ampere | R | Harmonic 17
8504 | 0x2138 | 4 | Complex | 0 | Ampere | R | Harmonic 19
8512 | 0x2140 | 4 | Complex | 1 | Ampere | R | Harmonic 1
8516 | 0x2144 | 4 | Complex | 1 | Ampere | R | Harmonic 2
8520 | 0x2148 | 4 | Complex | 1 | Ampere | R | Harmonic 3
8524 | 0x214C | 4 | Complex | 1 | Ampere | R | Harmonic 4
8528 | 0x2150 | 4 | Complex | 1 | Ampere | R | Harmonic 5
8532 | 0x2154 | 4 | Complex | 1 | Ampere | R | Harmonic 6
8536 | 0x2158 | 4 | Complex | 1 | Ampere | R | Harmonic 7
8540 | 0x215C | 4 | Complex | 1 | Ampere | R | Harmonic 8
8544 | 0x2160 | 4 | Complex | 1 | Ampere | R | Harmonic 9
8548 | 0x2164 | 4 | Complex | 1 | Ampere | R | Harmonic 10
8552 | 0x2168 | 4 | Complex | 1 | Ampere | R | Harmonic 11
8556 | 0x216C | 4 | Complex | 1 | Ampere | R | Harmonic 13
8560 | 0x2170 | 4 | Complex | 1 | Ampere | R | Harmonic 15
8564 | 0x2174 | 4 | Complex | 1 | Ampere | R | Harmonic 17
8568 | 0x2178 | 4 | Complex | 1 | Ampere | R | Harmonic 19
8576 | 0x2180 | 4 | Complex | 2 | Ampere | R | Harmonic 1
8580 | 0x2184 | 4 | Complex | 2 | Ampere | R | Harmonic 2
8584 | 0x2188 | 4 | Complex | 2 | Ampere | R | Harmonic 3
8588 | 0x218C | 4 | Complex | 2 | Ampere | R | Harmonic 4
8592 | 0x2190 | 4 | Complex | 2 | Ampere | R | Harmonic 5
8596 | 0x2194 | 4 | Complex | 2 | Ampere | R | Harmonic 6
8600 | 0x2198 | 4 | Complex | 2 | Ampere | R | Harmonic 7
8604 | 0x219C | 4 | Complex | 2 | Ampere | R | Harmonic 8
8608 | 0x21A0 | 4 | Complex | 2 | Ampere | R | Harmonic 9
8612 | 0x21A4 | 4 | Complex | 2 | Ampere | R | Harmonic 10
8616 | 0x21A8 | 4 | Complex | 2 | Ampere | R | Harmonic 11
8620 | 0x21AC | 4 | Complex | 2 | Ampere | R | Harmonic 13
8624 | 0x21B0 | 4 | Complex | 2 | Ampere | R | Harmonic 15
8628 | 0x21B4 | 4 | Complex | 2 | Ampere | R | Harmonic 17
8632 | 0x21B8 | 4 | Complex | 2 | Ampere | R | Harmonic 19
8640 | 0x21C0 | 4 | Complex | 3 | Ampere | R | Harmonic 1
8644 | 0x21C4 | 4 | Complex | 3 | Ampere | R | Harmonic 2
8648 | 0x21C8 | 4 | Complex | 3 | Ampere | R | Harmonic 3
8652 | 0x21CC | 4 | Complex | 3 | Ampere | R | Harmonic 4
8656 | 0x21D0 | 4 | Complex | 3 | Ampere | R | Harmonic 5
8660 | 0x21D4 | 4 | Complex | 3 | Ampere | R | Harmonic 6
8664 | 0x21D8 | 4 | Complex | 3 | Ampere | R | Harmonic 7
8668 | 0x21DC | 4 | Complex | 3 | Ampere | R | Harmonic 8
8672 | 0x21E0 | 4 | Complex | 3 | Ampere | R | Harmonic 9
8676 | 0x21E4 | 4 | Complex | 3 | Ampere | R | Harmonic 10
8680 | 0x21E8 | 4 | Complex | 3 | Ampere | R | Harmonic 11
8684 | 0x21EC | 4 | Complex | 3 | Ampere | R | Harmonic 13
8688 | 0x21F0 | 4 | Complex | 3 | Ampere | R | Harmonic 15
8692 | 0x21F4 | 4 | Complex | 3 | Ampere | R | Harmonic 17
8696 | 0x21F8 | 4 | Complex | 3 | Ampere | R | Harmonic 19
8704 | 0x2200 | 4 | Complex | 4 | Ampere | R | Harmonic 1
8708 | 0x2204 | 4 | Complex | 4 | Ampere | R | Harmonic 2
8712 | 0x2208 | 4 | Complex | 4 | Ampere | R | Harmonic 3
8716 | 0x220C | 4 | Complex | 4 | Ampere | R | Harmonic 4
8720 | 0x2210 | 4 | Complex | 4 | Ampere | R | Harmonic 5
8724 | 0x2214 | 4 | Complex | 4 | Ampere | R | Harmonic 6
8728 | 0x2218 | 4 | Complex | 4 | Ampere | R | Harmonic 7
8732 | 0x221C | 4 | Complex | 4 | Ampere | R | Harmonic 8
8736 | 0x2220 | 4 | Complex | 4 | Ampere | R | Harmonic 9
8740 | 0x2224 | 4 | Complex | 4 | Ampere | R | Harmonic 10
8744 | 0x2228 | 4 | Complex | 4 | Ampere | R | Harmonic 11
8748 | 0x222C | 4 | Complex | 4 | Ampere | R | Harmonic 13
8752 | 0x2230 | 4 | Complex | 4 | Ampere | R | Harmonic 15
8756 | 0x2234 | 4 | Complex | 4 | Ampere | R | Harmonic 17
8760 | 0x2238 | 4 | Complex | 4 | Ampere | R | Harmonic 19
8768 | 0x2240 | 4 | Complex | 5 | Ampere | R | Harmonic 1
8772 | 0x2244 | 4 | Complex | 5 | Ampere | R | Harmonic 2
8776 | 0x2248 | 4 | Complex | 5 | Ampere | R | Harmonic 3
8780 | 0x224C | 4 | Complex | 5 | Ampere | R | Harmonic 4
8784 | 0x2250 | 4 | Complex | 5 | Ampere | R | Harmonic 5
8788 | 0x2254 | 4 | Complex | 5 | Ampere | R | Harmonic 6
8792 | 0x2258 | 4 | Complex | 5 | Ampere | R | Harmonic 7
8796 | 0x225C | 4 | Complex | 5 | Ampere | R | Harmonic 8
8800 | 0x2260 | 4 | Complex | 5 | Ampere | R | Harmonic 9
8804 | 0x2264 | 4 | Complex | 5 | Ampere | R | Harmonic 10
8808 | 0x2268 | 4 | Complex | 5 | Ampere | R | Harmonic 11
8812 | 0x226C | 4 | Complex | 5 | Ampere | R | Harmonic 13
8816 | 0x2270 | 4 | Complex | 5 | Ampere | R | Harmonic 15
8820 | 0x2274 | 4 | Complex | 5 | Ampere | R | Harmonic 17
8824 | 0x2278 | 4 | Complex | 5 | Ampere | R | Harmonic 19
8832 | 0x2280 | 4 | Complex | 6 | Ampere | R | Harmonic 1
8836 | 0x2284 | 4 | Complex | 6 | Ampere | R | Harmonic 2
8840 | 0x2288 | 4 | Complex | 6 | Ampere | R | Harmonic 3
8844 | 0x228C | 4 | Complex | 6 | Ampere | R | Harmonic 4
8848 | 0x2290 | 4 | Complex | 6 | Ampere | R | Harmonic 5
8852 | 0x2294 | 4 | Complex | 6 | Ampere | R | Harmonic 6
8856 | 0x2298 | 4 | Complex | 6 | Ampere | R | Harmonic 7
8860 | 0x229C | 4 | Complex | 6 | Ampere | R | Harmonic 8
8864 | 0x22A0 | 4 | Complex | 6 | Ampere | R | Harmonic 9
8868 | 0x22A4 | 4 | Complex | 6 | Ampere | R | Harmonic 10
8872 | 0x22A8 | 4 | Complex | 6 | Ampere | R | Harmonic 11
8876 | 0x22AC | 4 | Complex | 6 | Ampere | R | Harmonic 13
8880 | 0x22B0 | 4 | Complex | 6 | Ampere | R | Harmonic 15
8884 | 0x22B4 | 4 | Complex | 6 | Ampere | R | Harmonic 17
8888 | 0x22B8 | 4 | Complex | 6 | Ampere | R | Harmonic 19
8896 | 0x22C0 | 4 | Complex | 7 | Ampere | R | Harmonic 1
8900 | 0x22C4 | 4 | Complex | 7 | Ampere | R | Harmonic 2
8904 | 0x22C8 | 4 | Complex | 7 | Ampere | R | Harmonic 3
8908 | 0x22CC | 4 | Complex | 7 | Ampere | R | Harmonic 4
8912 | 0x22D0 | 4 | Complex | 7 | Ampere | R | Harmonic 5
8916 | 0x22D4 | 4 | Complex | 7 | Ampere | R | Harmonic 6
8920 | 0x22D8 | 4 | Complex | 7 | Ampere | R | Harmonic 7
8924 | 0x22DC | 4 | Complex | 7 | Ampere | R | Harmonic 8
8928 | 0x22E0 | 4 | Complex | 7 | Ampere | R | Harmonic 9
8932 | 0x22E4 | 4 | Complex | 7 | Ampere | R | Harmonic 10
8936 | 0x22E8 | 4 | Complex | 7 | Ampere | R | Harmonic 11
8940 | 0x22EC | 4 | Complex | 7 | Ampere | R | Harmonic 13
8944 | 0x22F0 | 4 | Complex | 7 | Ampere | R | Harmonic 15
8948 | 0x22F4 | 4 | Complex | 7 | Ampere | R | Harmonic 17
8952 | 0x22F8 | 4 | Complex | 7 | Ampere | R | Harmonic 19
8960 | 0x2300 | 4 | Complex | 8 | Ampere | R | Harmonic 1
8964 | 0x2304 | 4 | Complex | 8 | Ampere | R | Harmonic 2
8968 | 0x2308 | 4 | Complex | 8 | Ampere | R | Harmonic 3
8972 | 0x230C | 4 | Complex | 8 | Ampere | R | Harmonic 4
8976 | 0x2310 | 4 | Complex | 8 | Ampere | R | Harmonic 5
8980 | 0x2314 | 4 | Complex | 8 | Ampere | R | Harmonic 6
8984 | 0x2318 | 4 | Complex | 8 | Ampere | R | Harmonic 7
8988 | 0x231C | 4 | Complex | 8 | Ampere | R | Harmonic 8
8992 | 0x2320 | 4 | Complex | 8 | Ampere | R | Harmonic 9
8996 | 0x2324 | 4 | Complex | 8 | Ampere | R | Harmonic 10
9000 | 0x2328 | 4 | Complex | 8 | Ampere | R | Harmonic 11
9004 | 0x232C | 4 | Complex | 8 | Ampere | R | Harmonic 13
9008 | 0x2330 | 4 | Complex | 8 | Ampere | R | Harmonic 15
9012 | 0x2334 | 4 | Complex | 8 | Ampere | R | Harmonic 17
9016 | 0x2338 | 4 | Complex | 8 | Ampere | R | Harmonic 19
9024 | 0x2340 | 4 | Complex | 9 | Ampere | R | Harmonic 1
9028 | 0x2344 | 4 | Complex | 9 | Ampere | R | Harmonic 2
9032 | 0x2348 | 4 | Complex | 9 | Ampere | R | Harmonic 3
9036 | 0x234C | 4 | Complex | 9 | Ampere | R | Harmonic 4
9040 | 0x2350 | 4 | Complex | 9 | Ampere | R | Harmonic 5
9044 | 0x2354 | 4 | Complex | 9 | Ampere | R | Harmonic 6
9048 | 0x2358 | 4 | Complex | 9 | Ampere | R | Harmonic 7
9052 | 0x235C | 4 | Complex | 9 | Ampere | R | Harmonic 8
9056 | 0x2360 | 4 | Complex | 9 | Ampere | R | Harmonic 9
9060 | 0x2364 | 4 | Complex | 9 | Ampere | R | Harmonic 10
9064 | 0x2368 | 4 | Complex | 9 | Ampere | R | Harmonic 11
9068 | 0x236C | 4 | Complex | 9 | Ampere | R | Harmonic 13
9072 | 0x2370 | 4 | Complex | 9 | Ampere | R | Harmonic 15
9076 | 0x2374 | 4 | Complex | 9 | Ampere | R | Harmonic 17
9080 | 0x2378 | 4 | Complex | 9 | Ampere | R | Harmonic 19
9088 | 0x2380 | 4 | Complex | 10 | Ampere | R | Harmonic 1
9092 | 0x2384 | 4 | Complex | 10 | Ampere | R | Harmonic 2
9096 | 0x2388 | 4 | Complex | 10 | Ampere | R | Harmonic 3
9100 | 0x238C | 4 | Complex | 10 | Ampere | R | Harmonic 4
9104 | 0x2390 | 4 | Complex | 10 | Ampere | R | Harmonic 5
9108 | 0x2394 | 4 | Complex | 10 | Ampere | R | Harmonic 6
9112 | 0x2398 | 4 | Complex | 10 | Ampere | R | Harmonic 7
9116 | 0x239C | 4 | Complex | 10 | Ampere | R | Harmonic 8
9120 | 0x23A0 | 4 | Complex | 10 | Ampere | R | Harmonic 9
9124 | 0x23A4 | 4 | Complex | 10 | Ampere | R | Harmonic 10
9128 | 0x23A8 | 4 | Complex | 10 | Ampere | R | Harmonic 11
9132 | 0x23AC | 4 | Complex | 10 | Ampere | R | Harmonic 13
9136 | 0x23B0 | 4 | Complex | 10 | Ampere | R | Harmonic 15
9140 | 0x23B4 | 4 | Complex | 10 | Ampere | R | Harmonic 17
9144 | 0x23B8 | 4 | Complex | 10 | Ampere | R | Harmonic 19
9152 | 0x23C0 | 4 | Complex | 11 | Ampere | R | Harmonic 1
9156 | 0x23C4 | 4 | Complex | 11 | Ampere | R | Harmonic 2
9160 | 0x23C8 | 4 | Complex | 11 | Ampere | R | Harmonic 3
9164 | 0x23CC | 4 | Complex | 11 | Ampere | R | Harmonic 4
9168 | 0x23D0 | 4 | Complex | 11 | Ampere | R | Harmonic 5
9172 | 0x23D4 | 4 | Complex | 11 | Ampere | R | Harmonic 6
9176 | 0x23D8 | 4 | Complex | 11 | Ampere | R | Harmonic 7
9180 | 0x23DC | 4 | Complex | 11 | Ampere | R | Harmonic 8
9184 | 0x23E0 | 4 | Complex | 11 | Ampere | R | Harmonic 9
9188 | 0x23E4 | 4 | Complex | 11 | Ampere | R | Harmonic 10
9192 | 0x23E8 | 4 | Complex | 11 | Ampere | R | Harmonic 11
9196 | 0x23EC | 4 | Complex | 11 | Ampere | R | Harmonic 13
9200 | 0x23F0 | 4 | Complex | 11 | Ampere | R | Harmonic 15
9204 | 0x23F4 | 4 | Complex | 11 | Ampere | R | Harmonic 17
9208 | 0x23F8 | 4 | Complex | 11 | Ampere | R | Harmonic 19
9216 | 0x2400 | 4 | Complex | 12 | Ampere | R | Harmonic 1
9220 | 0x2404 | 4 | Complex | 12 | Ampere | R | Harmonic 2
9224 | 0x2408 | 4 | Complex | 12 | Ampere | R | Harmonic 3
9228 | 0x240C | 4 | Complex | 12 | Ampere | R | Harmonic 4
9232 | 0x2410 | 4 | Complex | 12 | Ampere | R | Harmonic 5
9236 | 0x2414 | 4 | Complex | 12 | Ampere | R | Harmonic 6
9240 | 0x2418 | 4 | Complex | 12 | Ampere | R | Harmonic 7
9244 | 0x241C | 4 | Complex | 12 | Ampere | R | Harmonic 8
9248 | 0x2420 | 4 | Complex | 12 | Ampere | R | Harmonic 9
9252 | 0x2424 | 4 | Complex | 12 | Ampere | R | Harmonic 10
9256 | 0x2428 | 4 | Complex | 12 | Ampere | R | Harmonic 11
9260 | 0x242C | 4 | Complex | 12 | Ampere | R | Harmonic 13
9264 | 0x2430 | 4 | Complex | 12 | Ampere | R | Harmonic 15
9268 | 0x2434 | 4 | Complex | 12 | Ampere | R | Harmonic 17
9272 | 0x2438 | 4 | Complex | 12 | Ampere | R | Harmonic 19
9280 | 0x2440 | 4 | Complex | 13 | Ampere | R | Harmonic 1
9284 | 0x2444 | 4 | Complex | 13 | Ampere | R | Harmonic 2
9288 | 0x2448 | 4 | Complex | 13 | Ampere | R | Harmonic 3
9292 | 0x244C | 4 | Complex | 13 | Ampere | R | Harmonic 4
9296 | 0x2450 | 4 | Complex | 13 | Ampere | R | Harmonic 5
9300 | 0x2454 | 4 | Complex | 13 | Ampere | R | Harmonic 6
9304 | 0x2458 | 4 | Complex | 13 | Ampere | R | Harmonic 7
9308 | 0x245C | 4 | Complex | 13 | Ampere | R | Harmonic 8
9312 | 0x2460 | 4 | Complex | 13 | Ampere | R | Harmonic 9
9316 | 0x2464 | 4 | Complex | 13 | Ampere | R | Harmonic 10
9320 | 0x2468 | 4 | Complex | 13 | Ampere | R | Harmonic 11
9324 | 0x246C | 4 | Complex | 13 | Ampere | R | Harmonic 13
9328 | 0x2470 | 4 | Complex | 13 | Ampere | R | Harmonic 15
9332 | 0x2474 | 4 | Complex | 13 | Ampere | R | Harmonic 17
9336 | 0x2478 | 4 | Complex | 13 | Ampere | R | Harmonic 19
9344 | 0x2480 | 4 | Complex | 14 | Ampere | R | Harmonic 1
9348 | 0x2484 | 4 | Complex | 14 | Ampere | R | Harmonic 2
9352 | 0x2488 | 4 | Complex | 14 | Ampere | R | Harmonic 3
9356 | 0x248C | 4 | Complex | 14 | Ampere | R | Harmonic 4
9360 | 0x2490 | 4 | Complex | 14 | Ampere | R | Harmonic 5
9364 | 0x2494 | 4 | Complex | 14 | Ampere | R | Harmonic 6
9368 | 0x2498 | 4 | Complex | 14 | Ampere | R | Harmonic 7
9372 | 0x249C | 4 | Complex | 14 | Ampere | R | Harmonic 8
9376 | 0x24A0 | 4 | Complex | 14 | Ampere | R | Harmonic 9
9380 | 0x24A4 | 4 | Complex | 14 | Ampere | R | Harmonic 10
9384 | 0x24A8 | 4 | Complex | 14 | Ampere | R | Harmonic 11
9388 | 0x24AC | 4 | Complex | 14 | Ampere | R | Harmonic 13
9392 | 0x24B0 | 4 | Complex | 14 | Ampere | R | Harmonic 15
9396 | 0x24B4 | 4 | Complex | 14 | Ampere | R | Harmonic 17
9400 | 0x24B8 | 4 | Complex | 14 | Ampere | R | Harmonic 19
9408 | 0x24C0 | 4 | Complex | 15 | Ampere | R | Harmonic 1
9412 | 0x24C4 | 4 | Complex | 15 | Ampere | R | Harmonic 2
9416 | 0x24C8 | 4 | Complex | 15 | Ampere | R | Harmonic 3
9420 | 0x24CC | 4 | Complex | 15 | Ampere | R | Harmonic 4
9424 | 0x24D0 | 4 | Complex | 15 | Ampere | R | Harmonic 5
9428 | 0x24D4 | 4 | Complex | 15 | Ampere | R | Harmonic 6
9432 | 0x24D8 | 4 | Complex | 15 | Ampere | R | Harmonic 7
9436 | 0x24DC | 4 | Complex | 15 | Ampere | R | Harmonic 8
9440 | 0x24E0 | 4 | Complex | 15 | Ampere | R | Harmonic 9
9444 | 0x24E4 | 4 | Complex | 15 | Ampere | R | Harmonic 10
9448 | 0x24E8 | 4 | Complex | 15 | Ampere | R | Harmonic 11
9452 | 0x24EC | 4 | Complex | 15 | Ampere | R | Harmonic 13
9456 | 0x24F0 | 4 | Complex | 15 | Ampere | R | Harmonic 15
9460 | 0x24F4 | 4 | Complex | 15 | Ampere | R | Harmonic 17
9464 | 0x24F8 | 4 | Complex | 15 | Ampere | R | Harmonic 19
9472 | 0x2500 | 4 | Complex | 16 | Ampere | R | Harmonic 1
9476 | 0x2504 | 4 | Complex | 16 | Ampere | R | Harmonic 2
9480 | 0x2508 | 4 | Complex | 16 | Ampere | R | Harmonic 3
9484 | 0x250C | 4 | Complex | 16 | Ampere | R | Harmonic 4
9488 | 0x2510 | 4 | Complex | 16 | Ampere | R | Harmonic 5
9492 | 0x2514 | 4 | Complex | 16 | Ampere | R | Harmonic 6
9496 | 0x2518 | 4 | Complex | 16 | Ampere | R | Harmonic 7
9500 | 0x251C | 4 | Complex | 16 | Ampere | R | Harmonic 8
9504 | 0x2520 | 4 | Complex | 16 | Ampere | R | Harmonic 9
9508 | 0x2524 | 4 | Complex | 16 | Ampere | R | Harmonic 10
9512 | 0x2528 | 4 | Complex | 16 | Ampere | R | Harmonic 11
9516 | 0x252C | 4 | Complex | 16 | Ampere | R | Harmonic 13
9520 | 0x2530 | 4 | Complex | 16 | Ampere | R | Harmonic 15
9524 | 0x2534 | 4 | Complex | 16 | Ampere | R | Harmonic 17
9528 | 0x2538 | 4 | Complex | 16 | Ampere | R | Harmonic 19
9536 | 0x2540 | 4 | Complex | 17 | Ampere | R | Harmonic 1
9540 | 0x2544 | 4 | Complex | 17 | Ampere | R | Harmonic 2
9544 | 0x2548 | 4 | Complex | 17 | Ampere | R | Harmonic 3
9548 | 0x254C | 4 | Complex | 17 | Ampere | R | Harmonic 4
9552 | 0x2550 | 4 | Complex | 17 | Ampere | R | Harmonic 5
9556 | 0x2554 | 4 | Complex | 17 | Ampere | R | Harmonic 6
9560 | 0x2558 | 4 | Complex | 17 | Ampere | R | Harmonic 7
9564 | 0x255C | 4 | Complex | 17 | Ampere | R | Harmonic 8
9568 | 0x2560 | 4 | Complex | 17 | Ampere | R | Harmonic 9
9572 | 0x2564 | 4 | Complex | 17 | Ampere | R | Harmonic 10
9576 | 0x2568 | 4 | Complex | 17 | Ampere | R | Harmonic 11
9580 | 0x256C | 4 | Complex | 17 | Ampere | R | Harmonic 13
9584 | 0x2570 | 4 | Complex | 17 | Ampere | R | Harmonic 15
9588 | 0x2574 | 4 | Complex | 17 | Ampere | R | Harmonic 17
9592 | 0x2578 | 4 | Complex | 17 | Ampere | R | Harmonic 19
9600 | 0x2580 | 4 | Complex | 18 | Ampere | R | Harmonic 1
9604 | 0x2584 | 4 | Complex | 18 | Ampere | R | Harmonic 2
9608 | 0x2588 | 4 | Complex | 18 | Ampere | R | Harmonic 3
9612 | 0x258C | 4 | Complex | 18 | Ampere | R | Harmonic 4
9616 | 0x2590 | 4 | Complex | 18 | Ampere | R | Harmonic 5
9620 | 0x2594 | 4 | Complex | 18 | Ampere | R | Harmonic 6
9624 | 0x2598 | 4 | Complex | 18 | Ampere | R | Harmonic 7
9628 | 0x259C | 4 | Complex | 18 | Ampere | R | Harmonic 8
9632 | 0x25A0 | 4 | Complex | 18 | Ampere | R | Harmonic 9
9636 | 0x25A4 | 4 | Complex | 18 | Ampere | R | Harmonic 10
9640 | 0x25A8 | 4 | Complex | 18 | Ampere | R | Harmonic 11
9644 | 0x25AC | 4 | Complex | 18 | Ampere | R | Harmonic 13
9648 | 0x25B0 | 4 | Complex | 18 | Ampere | R | Harmonic 15
9652 | 0x25B4 | 4 | Complex | 18 | Ampere | R | Harmonic 17
9656 | 0x25B8 | 4 | Complex | 18 | Ampere | R | Harmonic 19
9664 | 0x25C0 | 4 | Complex | 19 | Ampere | R | Harmonic 1
9668 | 0x25C4 | 4 | Complex | 19 | Ampere | R | Harmonic 2
9672 | 0x25C8 | 4 | Complex | 19 | Ampere | R | Harmonic 3
9676 | 0x25CC | 4 | Complex | 19 | Ampere | R | Harmonic 4
9680 | 0x25D0 | 4 | Complex | 19 | Ampere | R | Harmonic 5
9684 | 0x25D4 | 4 | Complex | 19 | Ampere | R | Harmonic 6
9688 | 0x25D8 | 4 | Complex | 19 | Ampere | R | Harmonic 7
9692 | 0x25DC | 4 | Complex | 19 | Ampere | R | Harmonic 8
9696 | 0x25E0 | 4 | Complex | 19 | Ampere | R | Harmonic 9
9700 | 0x25E4 | 4 | Complex | 19 | Ampere | R | Harmonic 10
9704 | 0x25E8 | 4 | Complex | 19 | Ampere | R | Harmonic 11
9708 | 0x25EC | 4 | Complex | 19 | Ampere | R | Harmonic 13
9712 | 0x25F0 | 4 | Complex | 19 | Ampere | R | Harmonic 15
9716 | 0x25F4 | 4 | Complex | 19 | Ampere | R | Harmonic 17
9720 | 0x25F8 | 4 | Complex | 19 | Ampere | R | Harmonic 19
9728 | 0x2600 | 4 | Complex | 20 | Ampere | R | Harmonic 1
9732 | 0x2604 | 4 | Complex | 20 | Ampere | R | Harmonic 2
9736 | 0x2608 | 4 | Complex | 20 | Ampere | R | Harmonic 3
9740 | 0x260C | 4 | Complex | 20 | Ampere | R | Harmonic 4
9744 | 0x2610 | 4 | Complex | 20 | Ampere | R | Harmonic 5
9748 | 0x2614 | 4 | Complex | 20 | Ampere | R | Harmonic 6
9752 | 0x2618 | 4 | Complex | 20 | Ampere | R | Harmonic 7
9756 | 0x261C | 4 | Complex | 20 | Ampere | R | Harmonic 8
9760 | 0x2620 | 4 | Complex | 20 | Ampere | R | Harmonic 9
9764 | 0x2624 | 4 | Complex | 20 | Ampere | R | Harmonic 10
9768 | 0x2628 | 4 | Complex | 20 | Ampere | R | Harmonic 11
9772 | 0x262C | 4 | Complex | 20 | Ampere | R | Harmonic 13
9776 | 0x2630 | 4 | Complex | 20 | Ampere | R | Harmonic 15
9780 | 0x2634 | 4 | Complex | 20 | Ampere | R | Harmonic 17
9784 | 0x2638 | 4 | Complex | 20 | Ampere | R | Harmonic 19
9792 | 0x2640 | 4 | Complex | 21 | Ampere | R | Harmonic 1
9796 | 0x2644 | 4 | Complex | 21 | Ampere | R | Harmonic 2
9800 | 0x2648 | 4 | Complex | 21 | Ampere | R | Harmonic 3
9804 | 0x264C | 4 | Complex | 21 | Ampere | R | Harmonic 4
9808 | 0x2650 | 4 | Complex | 21 | Ampere | R | Harmonic 5
9812 | 0x2654 | 4 | Complex | 21 | Ampere | R | Harmonic 6
9816 | 0x2658 | 4 | Complex | 21 | Ampere | R | Harmonic 7
9820 | 0x265C | 4 | Complex | 21 | Ampere | R | Harmonic 8
9824 | 0x2660 | 4 | Complex | 21 | Ampere | R | Harmonic 9
9828 | 0x2664 | 4 | Complex | 21 | Ampere | R | Harmonic 10
9832 | 0x2668 | 4 | Complex | 21 | Ampere | R | Harmonic 11
9836 | 0x266C | 4 | Complex | 21 | Ampere | R | Harmonic 13
9840 | 0x2670 | 4 | Complex | 21 | Ampere | R | Harmonic 15
9844 | 0x2674 | 4 | Complex | 21 | Ampere | R | Harmonic 17
9848 | 0x2678 | 4 | Complex | 21 | Ampere | R | Harmonic 19
9856 | 0x2680 | 4 | Complex | 22 | Ampere | R | Harmonic 1
9860 | 0x2684 | 4 | Complex | 22 | Ampere | R | Harmonic 2
9864 | 0x2688 | 4 | Complex | 22 | Ampere | R | Harmonic 3
9868 | 0x268C | 4 | Complex | 22 | Ampere | R | Harmonic 4
9872 | 0x2690 | 4 | Complex | 22 | Ampere | R | Harmonic 5
9876 | 0x2694 | 4 | Complex | 22 | Ampere | R | Harmonic 6
9880 | 0x2698 | 4 | Complex | 22 | Ampere | R | Harmonic 7
9884 | 0x269C | 4 | Complex | 22 | Ampere | R | Harmonic 8
9888 | 0x26A0 | 4 | Complex | 22 | Ampere | R | Harmonic 9
9892 | 0x26A4 | 4 | Complex | 22 | Ampere | R | Harmonic 10
9896 | 0x26A8 | 4 | Complex | 22 | Ampere | R | Harmonic 11
9900 | 0x26AC | 4 | Complex | 22 | Ampere | R | Harmonic 13
9904 | 0x26B0 | 4 | Complex | 22 | Ampere | R | Harmonic 15
9908 | 0x26B4 | 4 | Complex | 22 | Ampere | R | Harmonic 17
9912 | 0x26B8 | 4 | Complex | 22 | Ampere | R | Harmonic 19
9920 | 0x26C0 | 4 | Complex | 23 | Ampere | R | Harmonic 1
9924 | 0x26C4 | 4 | Complex | 23 | Ampere | R | Harmonic 2
9928 | 0x26C8 | 4 | Complex | 23 | Ampere | R | Harmonic 3
9932 | 0x26CC | 4 | Complex | 23 | Ampere | R | Harmonic 4
9936 | 0x26D0 | 4 | Complex | 23 | Ampere | R | Harmonic 5
9940 | 0x26D4 | 4 | Complex | 23 | Ampere | R | Harmonic 6
9944 | 0x26D8 | 4 | Complex | 23 | Ampere | R | Harmonic 7
9948 | 0x26DC | 4 | Complex | 23 | Ampere | R | Harmonic 8
9952 | 0x26E0 | 4 | Complex | 23 | Ampere | R | Harmonic 9
9956 | 0x26E4 | 4 | Complex | 23 | Ampere | R | Harmonic 10
9960 | 0x26E8 | 4 | Complex | 23 | Ampere | R | Harmonic 11
9964 | 0x26EC | 4 | Complex | 23 | Ampere | R | Harmonic 13
9968 | 0x26F0 | 4 | Complex | 23 | Ampere | R | Harmonic 15
9972 | 0x26F4 | 4 | Complex | 23 | Ampere | R | Harmonic 17
9976 | 0x26F8 | 4 | Complex | 23 | Ampere | R | Harmonic 19
9984 | 0x2700 | 4 | Complex | 24 | Ampere | R | Harmonic 1
9988 | 0x2704 | 4 | Complex | 24 | Ampere | R | Harmonic 2
9992 | 0x2708 | 4 | Complex | 24 | Ampere | R | Harmonic 3
9996 | 0x270C | 4 | Complex | 24 | Ampere | R | Harmonic 4
10000 | 0x2710 | 4 | Complex | 24 | Ampere | R | Harmonic 5
10004 | 0x2714 | 4 | Complex | 24 | Ampere | R | Harmonic 6
10008 | 0x2718 | 4 | Complex | 24 | Ampere | R | Harmonic 7
10012 | 0x271C | 4 | Complex | 24 | Ampere | R | Harmonic 8
10016 | 0x2720 | 4 | Complex | 24 | Ampere | R | Harmonic 9
10020 | 0x2724 | 4 | Complex | 24 | Ampere | R | Harmonic 10
10024 | 0x2728 | 4 | Complex | 24 | Ampere | R | Harmonic 11
10028 | 0x272C | 4 | Complex | 24 | Ampere | R | Harmonic 13
10032 | 0x2730 | 4 | Complex | 24 | Ampere | R | Harmonic 15
10036 | 0x2734 | 4 | Complex | 24 | Ampere | R | Harmonic 17
10040 | 0x2738 | 4 | Complex | 24 | Ampere | R | Harmonic 19
10048 | 0x2740 | 4 | Complex | 25 | Ampere | R | Harmonic 1
10052 | 0x2744 | 4 | Complex | 25 | Ampere | R | Harmonic 2
10056 | 0x2748 | 4 | Complex | 25 | Ampere | R | Harmonic 3
10060 | 0x274C | 4 | Complex | 25 | Ampere | R | Harmonic 4
10064 | 0x2750 | 4 | Complex | 25 | Ampere | R | Harmonic 5
10068 | 0x2754 | 4 | Complex | 25 | Ampere | R | Harmonic 6
10072 | 0x2758 | 4 | Complex | 25 | Ampere | R | Harmonic 7
10076 | 0x275C | 4 | Complex | 25 | Ampere | R | Harmonic 8
10080 | 0x2760 | 4 | Complex | 25 | Ampere | R | Harmonic 9
10084 | 0x2764 | 4 | Complex | 25 | Ampere | R | Harmonic 10
10088 | 0x2768 | 4 | Complex | 25 | Ampere | R | Harmonic 11
10092 | 0x276C | 4 | Complex | 25 | Ampere | R | Harmonic 13
10096 | 0x2770 | 4 | Complex | 25 | Ampere | R | Harmonic 15
10100 | 0x2774 | 4 | Complex | 25 | Ampere | R | Harmonic 17
10104 | 0x2778 | 4 | Complex | 25 | Ampere | R | Harmonic 19
10112 | 0x2780 | 4 | Complex | 26 | Ampere | R | Harmonic 1
10116 | 0x2784 | 4 | Complex | 26 | Ampere | R | Harmonic 2
10120 | 0x2788 | 4 | Complex | 26 | Ampere | R | Harmonic 3
10124 | 0x278C | 4 | Complex | 26 | Ampere | R | Harmonic 4
10128 | 0x2790 | 4 | Complex | 26 | Ampere | R | Harmonic 5
10132 | 0x2794 | 4 | Complex | 26 | Ampere | R | Harmonic 6
10136 | 0x2798 | 4 | Complex | 26 | Ampere | R | Harmonic 7
10140 | 0x279C | 4 | Complex | 26 | Ampere | R | Harmonic 8
10144 | 0x27A0 | 4 | Complex | 26 | Ampere | R | Harmonic 9
10148 | 0x27A4 | 4 | Complex | 26 | Ampere | R | Harmonic 10
10152 | 0x27A8 | 4 | Complex | 26 | Ampere | R | Harmonic 11
10156 | 0x27AC | 4 | Complex | 26 | Ampere | R | Harmonic 13
10160 | 0x27B0 | 4 | Complex | 26 | Ampere | R | Harmonic 15
10164 | 0x27B4 | 4 | Complex | 26 | Ampere | R | Harmonic 17
10168 | 0x27B8 | 4 | Complex | 26 | Ampere | R | Harmonic 19
10176 | 0x27C0 | 4 | Complex | 27 | Ampere | R | Harmonic 1
10180 | 0x27C4 | 4 | Complex | 27 | Ampere | R | Harmonic 2
10184 | 0x27C8 | 4 | Complex | 27 | Ampere | R | Harmonic 3
10188 | 0x27CC | 4 | Complex | 27 | Ampere | R | Harmonic 4
10192 | 0x27D0 | 4 | Complex | 27 | Ampere | R | Harmonic 5
10196 | 0x27D4 | 4 | Complex | 27 | Ampere | R | Harmonic 6
10200 | 0x27D8 | 4 | Complex | 27 | Ampere | R | Harmonic 7
10204 | 0x27DC | 4 | Complex | 27 | Ampere | R | Harmonic 8
10208 | 0x27E0 | 4 | Complex | 27 | Ampere | R | Harmonic 9
10212 | 0x27E4 | 4 | Complex | 27 | Ampere | R | Harmonic 10
10216 | 0x27E8 | 4 | Complex | 27 | Ampere | R | Harmonic 11
10220 | 0x27EC | 4 | Complex | 27 | Ampere | R | Harmonic 13
10224 | 0x27F0 | 4 | Complex | 27 | Ampere | R | Harmonic 15
10228 | 0x27F4 | 4 | Complex | 27 | Ampere | R | Harmonic 17
10232 | 0x27F8 | 4 | Complex | 27 | Ampere | R | Harmonic 19
10496 | 0x2900 | 4 | Complex | L1-N | Volt | R | Harmonic 1
10500 | 0x2904 | 4 | Complex | L2-N | Volt | R | Harmonic 1
10504 | 0x2908 | 4 | Complex | L3-N | Volt | R | Harmonic 1
10508 | 0x290C | 4 | Complex | 0 | Ampere | R | Harmonic 1
10512 | 0x2910 | 4 | Complex | 1 | Ampere | R | Harmonic 1
10516 | 0x2914 | 4 | Complex | 2 | Ampere | R | Harmonic 1
10520 | 0x2918 | 4 | Complex | 3 | Ampere | R | Harmonic 1
10524 | 0x291C | 4 | Complex | 4 | Ampere | R | Harmonic 1
10528 | 0x2920 | 4 | Complex | 5 | Ampere | R | Harmonic 1
10532 | 0x2924 | 4 | Complex | 6 | Ampere | R | Harmonic 1
10536 | 0x2928 | 4 | Complex | 7 | Ampere | R | Harmonic 1
10540 | 0x292C | 4 | Complex | 8 | Ampere | R | Harmonic 1
10544 | 0x2930 | 4 | Complex | 9 | Ampere | R | Harmonic 1
10548 | 0x2934 | 4 | Complex | 10 | Ampere | R | Harmonic 1
10552 | 0x2938 | 4 | Complex | 11 | Ampere | R | Harmonic 1
10556 | 0x293C | 4 | Complex | 12 | Ampere | R | Harmonic 1
10560 | 0x2940 | 4 | Complex | 13 | Ampere | R | Harmonic 1
10564 | 0x2944 | 4 | Complex | 14 | Ampere | R | Harmonic 1
10568 | 0x2948 | 4 | Complex | 15 | Ampere | R | Harmonic 1
10572 | 0x294C | 4 | Complex | 16 | Ampere | R | Harmonic 1
10576 | 0x2950 | 4 | Complex | 17 | Ampere | R | Harmonic 1
10580 | 0x2954 | 4 | Complex | 18 | Ampere | R | Harmonic 1
10584 | 0x2958 | 4 | Complex | 19 | Ampere | R | Harmonic 1
10588 | 0x295C | 4 | Complex | 20 | Ampere | R | Harmonic 1
10592 | 0x2960 | 4 | Complex | 21 | Ampere | R | Harmonic 1
10596 | 0x2964 | 4 | Complex | 22 | Ampere | R | Harmonic 1
10600 | 0x2968 | 4 | Complex | 23 | Ampere | R | Harmonic 1
10604 | 0x296C | 4 | Complex | 24 | Ampere | R | Harmonic 1
10608 | 0x2970 | 4 | Complex | 25 | Ampere | R | Harmonic 1
10612 | 0x2974 | 4 | Complex | 26 | Ampere | R | Harmonic 1
10616 | 0x2978 | 4 | Complex | 27 | Ampere | R | Harmonic 1

## General Configuration
Modbus Address | Modbus Address (Hex) | Size | Type | Channel | Unit | R/W | Description
4480 | 0x1180 | 1 | Int16 |  |  | RW | use phantom voltages, 0: disabled, 1: 3phase 120 degrees, 2: 2 phase 180 degrees, 3: virtual star point
4481 | 0x1181 | 1 | Int16 |  |  | RW | modbus address
5232 | 0x1470 | 2 | Float |  | VA | RW | start threshold for event detection
5234 | 0x1472 | 2 | Float |  | VA | RW | end threshold for event detection
5236 | 0x1474 | 2 | Float |  | VA | RW | extend threshold for event detection
5238 | 0x1476 | 1 | Int16 |  | 100 ms | RW | waiting period
5632 | 0x1600 | 2 | Float |  |  | R | Voltage L1 factory calibration factor
5634 | 0x1602 | 2 | Float |  |  | R | Voltage L2 factory calibration factor
5636 | 0x1604 | 2 | Float |  |  | R | Voltage L3 factory calibration factor
5638 | 0x1606 | 2 | Float |  |  | R | Voltage N factory calibration factor
5640 | 0x1608 | 2 | Float |  |  | RW | Voltage L1 calibration adjustment factor
5642 | 0x160A | 2 | Float |  |  | RW | Voltage L2 calibration adjustment factor
5644 | 0x160C | 2 | Float |  |  | RW | Voltage L3 calibration adjustment factor
5646 | 0x160E | 2 | Float |  |  | RW | Voltage N calibration adjustment factor
5664 | 0x1620 | 1 | Int16 |  |  | R | Device Type
5665 | 0x1621 | 1 | Int16 |  |  | R | Reserved
5666 | 0x1622 | 2 | Int32 |  |  | R | Serial Number
5668 | 0x1624 | 1 | Int16 |  |  | RW | Firmware minor version
5669 | 0x1625 | 1 | Int16 |  |  | RW | Firmware major version

## CT Configuration
Modbus Address | Modbus Address (Hex) | Size | Type | Channel | Unit | R/W | Description
4096 | 0x1000 | 1 | Int16 | 0 |  | RW | CT Associated Voltage | Phase | Normal | Reverse
4097 | 0x1001 | 1 | Int16 | 1 |  | RW | CT Associated Voltage | L1-N | 1 | 16
4098 | 0x1002 | 1 | Int16 | 2 |  | RW | CT Associated Voltage | L2-N | 2 | 32
4099 | 0x1003 | 1 | Int16 | 3 |  | RW | CT Associated Voltage | L3-N | 4 | 64
4100 | 0x1004 | 1 | Int16 | 4 |  | RW | CT Associated Voltage | L1-L2 | 33 | 18
4101 | 0x1005 | 1 | Int16 | 5 |  | RW | CT Associated Voltage | L2-L3 | 66 | 36
4102 | 0x1006 | 1 | Int16 | 6 |  | RW | CT Associated Voltage | L1-L3 | 65 | 20
4103 | 0x1007 | 1 | Int16 | 7 |  | RW | CT Associated Voltage
4104 | 0x1008 | 1 | Int16 | 8 |  | RW | CT Associated Voltage | Id | Type
4105 | 0x1009 | 1 | Int16 | 9 |  | RW | CT Associated Voltage | 0 | SCT01-50A, SCT01-100A, SCT01-200A
4106 | 0x100A | 1 | Int16 | 10 |  | RW | CT Associated Voltage | 1 | SCT01-400A and SCT01-800A
4107 | 0x100B | 1 | Int16 | 11 |  | RW | CT Associated Voltage | 2 | Rogowski coil 600A-100mV
4108 | 0x100C | 1 | Int16 | 12 |  | RW | CT Associated Voltage | 3 | SCT02-50A
4109 | 0x100D | 1 | Int16 | 13 |  | RW | CT Associated Voltage | 4 | SCT02-100A
4110 | 0x100E | 1 | Int16 | 14 |  | RW | CT Associated Voltage | 5 | SCT02-200A
4111 | 0x100F | 1 | Int16 | 15 |  | RW | CT Associated Voltage | 6 | SCT02-400A
4112 | 0x1010 | 1 | Int16 | 16 |  | RW | CT Associated Voltage | 7 | SCT02-800A
4113 | 0x1011 | 1 | Int16 | 17 |  | RW | CT Associated Voltage | 8 | SCT03-50A
4114 | 0x1012 | 1 | Int16 | 18 |  | RW | CT Associated Voltage | 9 | SCT03-100A
4115 | 0x1013 | 1 | Int16 | 19 |  | RW | CT Associated Voltage | 10 | SCT03-200A
4116 | 0x1014 | 1 | Int16 | 20 |  | RW | CT Associated Voltage | 11 | Rogowski coil 400A-100mV
4117 | 0x1015 | 1 | Int16 | 21 |  | RW | CT Associated Voltage | 12 | Closed CT
4118 | 0x1016 | 1 | Int16 | 22 |  | RW | CT Associated Voltage | 13 | No phase adjustment applied
4119 | 0x1017 | 1 | Int16 | 23 |  | RW | CT Associated Voltage | 14 | No shift correction applied
4120 | 0x1018 | 1 | Int16 | 24 |  | RW | CT Associated Voltage | 15 | Rogowski coil 200A
4121 | 0x1019 | 1 | Int16 | 25 |  | RW | CT Associated Voltage
4122 | 0x101A | 1 | Int16 | 26 |  | RW | CT Associated Voltage
4123 | 0x101B | 1 | Int16 | 27 |  | RW | CT Associated Voltage
4352 | 0x1100 | 1 | Int16 | 0 |  | RW | CT Type Identifier
4353 | 0x1101 | 1 | Int16 | 1 |  | RW | CT Type Identifier
4354 | 0x1102 | 1 | Int16 | 2 |  | RW | CT Type Identifier
4355 | 0x1103 | 1 | Int16 | 3 |  | RW | CT Type Identifier
4356 | 0x1104 | 1 | Int16 | 4 |  | RW | CT Type Identifier
4357 | 0x1105 | 1 | Int16 | 5 |  | RW | CT Type Identifier
4358 | 0x1106 | 1 | Int16 | 6 |  | RW | CT Type Identifier
4359 | 0x1107 | 1 | Int16 | 7 |  | RW | CT Type Identifier
4360 | 0x1108 | 1 | Int16 | 8 |  | RW | CT Type Identifier
4361 | 0x1109 | 1 | Int16 | 9 |  | RW | CT Type Identifier
4362 | 0x110A | 1 | Int16 | 10 |  | RW | CT Type Identifier
4363 | 0x110B | 1 | Int16 | 11 |  | RW | CT Type Identifier
4364 | 0x110C | 1 | Int16 | 12 |  | RW | CT Type Identifier
4365 | 0x110D | 1 | Int16 | 13 |  | RW | CT Type Identifier
4366 | 0x110E | 1 | Int16 | 14 |  | RW | CT Type Identifier
4367 | 0x110F | 1 | Int16 | 15 |  | RW | CT Type Identifier
4368 | 0x1110 | 1 | Int16 | 16 |  | RW | CT Type Identifier
4369 | 0x1111 | 1 | Int16 | 17 |  | RW | CT Type Identifier
4370 | 0x1112 | 1 | Int16 | 18 |  | RW | CT Type Identifier
4371 | 0x1113 | 1 | Int16 | 19 |  | RW | CT Type Identifier
4372 | 0x1114 | 1 | Int16 | 20 |  | RW | CT Type Identifier
4373 | 0x1115 | 1 | Int16 | 21 |  | RW | CT Type Identifier
4374 | 0x1116 | 1 | Int16 | 22 |  | RW | CT Type Identifier
4375 | 0x1117 | 1 | Int16 | 23 |  | RW | CT Type Identifier
4376 | 0x1118 | 1 | Int16 | 24 |  | RW | CT Type Identifier
4377 | 0x1119 | 1 | Int16 | 25 |  | RW | CT Type Identifier
4378 | 0x111A | 1 | Int16 | 26 |  | RW | CT Type Identifier
4379 | 0x111B | 1 | Int16 | 27 |  | RW | CT Type Identifier
4416 | 0x1140 | 1 | Int16 | 0 |  | RW | CT Slot Mapping
4417 | 0x1141 | 1 | Int16 | 1 |  | RW | CT Slot Mapping
4418 | 0x1142 | 1 | Int16 | 2 |  | RW | CT Slot Mapping
4419 | 0x1143 | 1 | Int16 | 3 |  | RW | CT Slot Mapping
4420 | 0x1144 | 1 | Int16 | 4 |  | RW | CT Slot Mapping
4421 | 0x1145 | 1 | Int16 | 5 |  | RW | CT Slot Mapping
4422 | 0x1146 | 1 | Int16 | 6 |  | RW | CT Slot Mapping
4423 | 0x1147 | 1 | Int16 | 7 |  | RW | CT Slot Mapping
4424 | 0x1148 | 1 | Int16 | 8 |  | RW | CT Slot Mapping
4425 | 0x1149 | 1 | Int16 | 9 |  | RW | CT Slot Mapping
4426 | 0x114A | 1 | Int16 | 10 |  | RW | CT Slot Mapping
4427 | 0x114B | 1 | Int16 | 11 |  | RW | CT Slot Mapping
4428 | 0x114C | 1 | Int16 | 12 |  | RW | CT Slot Mapping
4429 | 0x114D | 1 | Int16 | 13 |  | RW | CT Slot Mapping
4430 | 0x114E | 1 | Int16 | 14 |  | RW | CT Slot Mapping
4431 | 0x114F | 1 | Int16 | 15 |  | RW | CT Slot Mapping
4432 | 0x1150 | 1 | Int16 | 16 |  | RW | CT Slot Mapping
4433 | 0x1151 | 1 | Int16 | 17 |  | RW | CT Slot Mapping
4434 | 0x1152 | 1 | Int16 | 18 |  | RW | CT Slot Mapping
4435 | 0x1153 | 1 | Int16 | 19 |  | RW | CT Slot Mapping
4436 | 0x1154 | 1 | Int16 | 20 |  | RW | CT Slot Mapping
4437 | 0x1155 | 1 | Int16 | 21 |  | RW | CT Slot Mapping
4438 | 0x1156 | 1 | Int16 | 22 |  | RW | CT Slot Mapping
4439 | 0x1157 | 1 | Int16 | 23 |  | RW | CT Slot Mapping
4440 | 0x1158 | 1 | Int16 | 24 |  | RW | CT Slot Mapping
4441 | 0x1159 | 1 | Int16 | 25 |  | RW | CT Slot Mapping
4442 | 0x115A | 1 | Int16 | 26 |  | RW | CT Slot Mapping
4443 | 0x115B | 1 | Int16 | 27 |  | RW | CT Slot Mapping

## Virtual Channel Configuration
Modbus Address | Modbus Address (Hex) | Size | Type | Virtual channel | Unit | R/W | Description
5120 | 0x1400 | 2 | Int32 | 0 |  | RW | Positive CT mask
5122 | 0x1402 | 2 | Int32 | 0 |  | RW | Negative CT mask
5124 | 0x1404 | 2 | Int32 | 1 |  | RW | Positive CT mask
5126 | 0x1406 | 2 | Int32 | 1 |  | RW | Negative CT mask
5128 | 0x1408 | 2 | Int32 | 2 |  | RW | Positive CT mask
5130 | 0x140A | 2 | Int32 | 2 |  | RW | Negative CT mask
5132 | 0x140C | 2 | Int32 | 3 |  | RW | Positive CT mask
5134 | 0x140E | 2 | Int32 | 3 |  | RW | Negative CT mask
5136 | 0x1410 | 2 | Int32 | 4 |  | RW | Positive CT mask
5138 | 0x1412 | 2 | Int32 | 4 |  | RW | Negative CT mask
5140 | 0x1414 | 2 | Int32 | 5 |  | RW | Positive CT mask
5142 | 0x1416 | 2 | Int32 | 5 |  | RW | Negative CT mask
5144 | 0x1418 | 2 | Int32 | 6 |  | RW | Positive CT mask
5146 | 0x141A | 2 | Int32 | 6 |  | RW | Negative CT mask
5148 | 0x141C | 2 | Int32 | 7 |  | RW | Positive CT mask
5150 | 0x141E | 2 | Int32 | 7 |  | RW | Negative CT mask
5152 | 0x1420 | 2 | Int32 | 8 |  | RW | Positive CT mask
5154 | 0x1422 | 2 | Int32 | 8 |  | RW | Negative CT mask
5156 | 0x1424 | 2 | Int32 | 9 |  | RW | Positive CT mask
5158 | 0x1426 | 2 | Int32 | 9 |  | RW | Negative CT mask
5160 | 0x1428 | 2 | Int32 | 10 |  | RW | Positive CT mask
5162 | 0x142A | 2 | Int32 | 10 |  | RW | Negative CT mask
5164 | 0x142C | 2 | Int32 | 11 |  | RW | Positive CT mask
5166 | 0x142E | 2 | Int32 | 11 |  | RW | Negative CT mask
5168 | 0x1430 | 2 | Int32 | 12 |  | RW | Positive CT mask
5170 | 0x1432 | 2 | Int32 | 12 |  | RW | Negative CT mask
5172 | 0x1434 | 2 | Int32 | 13 |  | RW | Positive CT mask
5174 | 0x1436 | 2 | Int32 | 13 |  | RW | Negative CT mask

## Bus Info
Modbus Address | Modbus Address (Hex) | Size | Type | Device | Unit | R/W | Description
5248 | 0x1480 | 1 | Int16 | 0 |  | RW | Device Type, write 1 to remove device
5249 | 0x1481 | 1 | Int16 | 0 |  | R | Number of assigned slots
5250 | 0x1482 | 2 | Int32 | 0 |  | R | Serialnumber
5252 | 0x1484 | 1 | Int16 | 0 |  | RW | Firmware minor version
5253 | 0x1485 | 1 | Int16 | 0 |  | RW | Firmware major version
5254 | 0x1486 | 2 | Int32 | 0 |  | R | Status word
5256 | 0x1488 | 2 | Int32 | 0 |  | R | Last reading
5258 | 0x148A | 1 | Int16 | 0 |  | RW | Channel A slot id, write 1 to blink led, 0 to clear any blinking led
5259 | 0x148B | 1 | Int16 | 0 |  | RW | Channel B slot id, write 1 to blink led, 0 to clear any blinking led
5260 | 0x148C | 1 | Int16 | 0 |  | RW | Channel C slot id, write 1 to blink led, 0 to clear any blinking led
5261 | 0x148D | 1 | Int16 | 0 |  | RW | Channel D slot id, write 1 to blink led, 0 to clear any blinking led
5262 | 0x148E | 1 | Int16 | 0 |  | RW | Channel E slot id, write 1 to blink led, 0 to clear any blinking led
5263 | 0x148F | 1 | Int16 | 0 |  | RW | Channel F slot id, write 1 to blink led, 0 to clear any blinking led
5264 | 0x1490 | 1 | Int16 | 0 |  | RW | Channel G slot id, write 1 to blink led, 0 to clear any blinking led
5265 | 0x1491 | 1 | Int16 | 0 |  | RW | Channel H slot id, write 1 to blink led, 0 to clear any blinking led
5266 | 0x1492 | 1 | Int16 | 0 |  | R | Firmware upgrade status
5267 | 0x1493 | 1 | Int16 | 0 |  | RW | Channel I slot id, write 1 to blink led, 0 to clear any blinking led
5268 | 0x1494 | 1 | Int16 | 0 |  | RW | Channel J slot id, write 1 to blink led, 0 to clear any blinking led
5269 | 0x1495 | 1 | Int16 | 0 |  | RW | Channel K slot id, write 1 to blink led, 0 to clear any blinking led
5270 | 0x1496 | 1 | Int16 | 0 |  | RW | Channel L slot id, write 1 to blink led, 0 to clear any blinking led
5271 | 0x1497 | 1 | Int16 | 0 |  | RW | Channel M slot id, write 1 to blink led, 0 to clear any blinking led
5272 | 0x1498 | 1 | Int16 | 0 |  | RW | Channel N slot id, write 1 to blink led, 0 to clear any blinking led
5273 | 0x1499 | 1 | Int16 | 0 |  | RW | Channel O slot id, write 1 to blink led, 0 to clear any blinking led
5274 | 0x149A | 1 | Int16 | 0 |  | RW | Channel P slot id, write 1 to blink led, 0 to clear any blinking led
5280 | 0x14A0 | 1 | Int16 | 1 |  | RW | Device Type, write 1 to remove device
5281 | 0x14A1 | 1 | Int16 | 1 |  | R | Number of assigned slots
5282 | 0x14A2 | 2 | Int32 | 1 |  | R | Serialnumber
5284 | 0x14A4 | 1 | Int16 | 1 |  | RW | Firmware minor version
5285 | 0x14A5 | 1 | Int16 | 1 |  | RW | Firmware major version
5286 | 0x14A6 | 2 | Int32 | 1 |  | R | Status word
5288 | 0x14A8 | 2 | Int32 | 1 |  | R | Last reading
5290 | 0x14AA | 1 | Int16 | 1 |  | RW | Channel A slot id, write 1 to blink led, 0 to clear any blinking led
5291 | 0x14AB | 1 | Int16 | 1 |  | RW | Channel B slot id, write 1 to blink led, 0 to clear any blinking led
5292 | 0x14AC | 1 | Int16 | 1 |  | RW | Channel C slot id, write 1 to blink led, 0 to clear any blinking led
5293 | 0x14AD | 1 | Int16 | 1 |  | RW | Channel D slot id, write 1 to blink led, 0 to clear any blinking led
5294 | 0x14AE | 1 | Int16 | 1 |  | RW | Channel E slot id, write 1 to blink led, 0 to clear any blinking led
5295 | 0x14AF | 1 | Int16 | 1 |  | RW | Channel F slot id, write 1 to blink led, 0 to clear any blinking led
5296 | 0x14B0 | 1 | Int16 | 1 |  | RW | Channel G slot id, write 1 to blink led, 0 to clear any blinking led
5297 | 0x14B1 | 1 | Int16 | 1 |  | RW | Channel H slot id, write 1 to blink led, 0 to clear any blinking led
5298 | 0x14B2 | 1 | Int16 | 1 |  | R | Firmware upgrade status
5299 | 0x14B3 | 1 | Int16 | 1 |  | RW | Channel I slot id, write 1 to blink led, 0 to clear any blinking led
5300 | 0x14B4 | 1 | Int16 | 1 |  | RW | Channel J slot id, write 1 to blink led, 0 to clear any blinking led
5301 | 0x14B5 | 1 | Int16 | 1 |  | RW | Channel K slot id, write 1 to blink led, 0 to clear any blinking led
5302 | 0x14B6 | 1 | Int16 | 1 |  | RW | Channel L slot id, write 1 to blink led, 0 to clear any blinking led
5303 | 0x14B7 | 1 | Int16 | 1 |  | RW | Channel M slot id, write 1 to blink led, 0 to clear any blinking led
5304 | 0x14B8 | 1 | Int16 | 1 |  | RW | Channel N slot id, write 1 to blink led, 0 to clear any blinking led
5305 | 0x14B9 | 1 | Int16 | 1 |  | RW | Channel O slot id, write 1 to blink led, 0 to clear any blinking led
5306 | 0x14BA | 1 | Int16 | 1 |  | RW | Channel P slot id, write 1 to blink led, 0 to clear any blinking led
5312 | 0x14C0 | 1 | Int16 | 2 |  | RW | Device Type, write 1 to remove device
5313 | 0x14C1 | 1 | Int16 | 2 |  | RW | Number of assigned slots
5314 | 0x14C2 | 2 | Int32 | 2 |  | R | Serialnumber
5316 | 0x14C4 | 1 | Int16 | 2 |  | RW | Firmware minor version
5317 | 0x14C5 | 1 | Int16 | 2 |  | RW | Firmware major version
5318 | 0x14C6 | 2 | Int32 | 2 |  | R | Status word
5320 | 0x14C8 | 2 | Int32 | 2 |  | R | Last reading
5322 | 0x14CA | 1 | Int16 | 2 |  | RW | Channel A slot id, write 1 to blink led, 0 to clear any blinking led
5323 | 0x14CB | 1 | Int16 | 2 |  | RW | Channel B slot id, write 1 to blink led, 0 to clear any blinking led
5324 | 0x14CC | 1 | Int16 | 2 |  | RW | Channel C slot id, write 1 to blink led, 0 to clear any blinking led
5325 | 0x14CD | 1 | Int16 | 2 |  | RW | Channel D slot id, write 1 to blink led, 0 to clear any blinking led
5326 | 0x14CE | 1 | Int16 | 2 |  | RW | Channel E slot id, write 1 to blink led, 0 to clear any blinking led
5327 | 0x14CF | 1 | Int16 | 2 |  | RW | Channel F slot id, write 1 to blink led, 0 to clear any blinking led
5328 | 0x14D0 | 1 | Int16 | 2 |  | RW | Channel G slot id, write 1 to blink led, 0 to clear any blinking led
5329 | 0x14D1 | 1 | Int16 | 2 |  | RW | Channel H slot id, write 1 to blink led, 0 to clear any blinking led
5330 | 0x14D2 | 1 | Int16 | 2 |  | R | Firmware upgrade status
5331 | 0x14D3 | 1 | Int16 | 2 |  | RW | Channel I slot id, write 1 to blink led, 0 to clear any blinking led
5332 | 0x14D4 | 1 | Int16 | 2 |  | RW | Channel J slot id, write 1 to blink led, 0 to clear any blinking led
5333 | 0x14D5 | 1 | Int16 | 2 |  | RW | Channel K slot id, write 1 to blink led, 0 to clear any blinking led
5334 | 0x14D6 | 1 | Int16 | 2 |  | RW | Channel L slot id, write 1 to blink led, 0 to clear any blinking led
5335 | 0x14D7 | 1 | Int16 | 2 |  | RW | Channel M slot id, write 1 to blink led, 0 to clear any blinking led
5336 | 0x14D8 | 1 | Int16 | 2 |  | RW | Channel N slot id, write 1 to blink led, 0 to clear any blinking led
5337 | 0x14D9 | 1 | Int16 | 2 |  | RW | Channel O slot id, write 1 to blink led, 0 to clear any blinking led
5338 | 0x14DA | 1 | Int16 | 2 |  | RW | Channel P slot id, write 1 to blink led, 0 to clear any blinking led
5344 | 0x14E0 | 1 | Int16 | 3 |  | RW | Device Type, write 1 to remove device
5345 | 0x14E1 | 1 | Int16 | 3 |  | R | Number of assigned slots
5346 | 0x14E2 | 2 | Int32 | 3 |  | R | Serialnumber
5348 | 0x14E4 | 1 | Int16 | 3 |  | RW | Firmware minor version
5349 | 0x14E5 | 1 | Int16 | 3 |  | RW | Firmware major version
5350 | 0x14E6 | 2 | Int32 | 3 |  | R | Status word
5352 | 0x14E8 | 2 | Int32 | 3 |  | R | Last reading
5354 | 0x14EA | 1 | Int16 | 3 |  | RW | Channel A slot id, write 1 to blink led, 0 to clear any blinking led
5355 | 0x14EB | 1 | Int16 | 3 |  | RW | Channel B slot id, write 1 to blink led, 0 to clear any blinking led
5356 | 0x14EC | 1 | Int16 | 3 |  | RW | Channel C slot id, write 1 to blink led, 0 to clear any blinking led
5357 | 0x14ED | 1 | Int16 | 3 |  | RW | Channel D slot id, write 1 to blink led, 0 to clear any blinking led
5358 | 0x14EE | 1 | Int16 | 3 |  | RW | Channel E slot id, write 1 to blink led, 0 to clear any blinking led
5359 | 0x14EF | 1 | Int16 | 3 |  | RW | Channel F slot id, write 1 to blink led, 0 to clear any blinking led
5360 | 0x14F0 | 1 | Int16 | 3 |  | RW | Channel G slot id, write 1 to blink led, 0 to clear any blinking led
5361 | 0x14F1 | 1 | Int16 | 3 |  | RW | Channel H slot id, write 1 to blink led, 0 to clear any blinking led
5362 | 0x14F2 | 1 | Int16 | 3 |  | R | Firmware upgrade status
5363 | 0x14F3 | 1 | Int16 | 3 |  | RW | Channel I slot id, write 1 to blink led, 0 to clear any blinking led
5364 | 0x14F4 | 1 | Int16 | 3 |  | RW | Channel J slot id, write 1 to blink led, 0 to clear any blinking led
5365 | 0x14F5 | 1 | Int16 | 3 |  | RW | Channel K slot id, write 1 to blink led, 0 to clear any blinking led
5366 | 0x14F6 | 1 | Int16 | 3 |  | RW | Channel L slot id, write 1 to blink led, 0 to clear any blinking led
5367 | 0x14F7 | 1 | Int16 | 3 |  | RW | Channel M slot id, write 1 to blink led, 0 to clear any blinking led
5368 | 0x14F8 | 1 | Int16 | 3 |  | RW | Channel N slot id, write 1 to blink led, 0 to clear any blinking led
5369 | 0x14F9 | 1 | Int16 | 3 |  | RW | Channel O slot id, write 1 to blink led, 0 to clear any blinking led
5370 | 0x14FA | 1 | Int16 | 3 |  | RW | Channel P slot id, write 1 to blink led, 0 to clear any blinking led
5376 | 0x1500 | 1 | Int16 | 4 |  | RW | Device Type, write 1 to remove device
5377 | 0x1501 | 1 | Int16 | 4 |  | RW | Number of assigned slots
5378 | 0x1502 | 2 | Int32 | 4 |  | R | Serialnumber
5380 | 0x1504 | 1 | Int16 | 4 |  | RW | Firmware minor version
5381 | 0x1505 | 1 | Int16 | 4 |  | RW | Firmware major version
5382 | 0x1506 | 2 | Int32 | 4 |  | R | Status word
5384 | 0x1508 | 2 | Int32 | 4 |  | R | Last reading
5386 | 0x150A | 1 | Int16 | 4 |  | RW | Channel A slot id, write 1 to blink led, 0 to clear any blinking led
5387 | 0x150B | 1 | Int16 | 4 |  | RW | Channel B slot id, write 1 to blink led, 0 to clear any blinking led
5388 | 0x150C | 1 | Int16 | 4 |  | RW | Channel C slot id, write 1 to blink led, 0 to clear any blinking led
5389 | 0x150D | 1 | Int16 | 4 |  | RW | Channel D slot id, write 1 to blink led, 0 to clear any blinking led
5390 | 0x150E | 1 | Int16 | 4 |  | RW | Channel E slot id, write 1 to blink led, 0 to clear any blinking led
5391 | 0x150F | 1 | Int16 | 4 |  | RW | Channel F slot id, write 1 to blink led, 0 to clear any blinking led
5392 | 0x1510 | 1 | Int16 | 4 |  | RW | Channel G slot id, write 1 to blink led, 0 to clear any blinking led
5393 | 0x1511 | 1 | Int16 | 4 |  | RW | Channel H slot id, write 1 to blink led, 0 to clear any blinking led
5394 | 0x1512 | 1 | Int16 | 4 |  | R | Firmware upgrade status
5395 | 0x1513 | 1 | Int16 | 4 |  | RW | Channel I slot id, write 1 to blink led, 0 to clear any blinking led
5396 | 0x1514 | 1 | Int16 | 4 |  | RW | Channel J slot id, write 1 to blink led, 0 to clear any blinking led
5397 | 0x1515 | 1 | Int16 | 4 |  | RW | Channel K slot id, write 1 to blink led, 0 to clear any blinking led
5398 | 0x1516 | 1 | Int16 | 4 |  | RW | Channel L slot id, write 1 to blink led, 0 to clear any blinking led
5399 | 0x1517 | 1 | Int16 | 4 |  | RW | Channel M slot id, write 1 to blink led, 0 to clear any blinking led
5400 | 0x1518 | 1 | Int16 | 4 |  | RW | Channel N slot id, write 1 to blink led, 0 to clear any blinking led
5401 | 0x1519 | 1 | Int16 | 4 |  | RW | Channel O slot id, write 1 to blink led, 0 to clear any blinking led
5402 | 0x151A | 1 | Int16 | 4 |  | RW | Channel P slot id, write 1 to blink led, 0 to clear any blinking led
5408 | 0x1520 | 1 | Int16 | 5 |  | RW | Device Type, write 1 to remove device
5409 | 0x1521 | 1 | Int16 | 5 |  | R | Number of assigned slots
5410 | 0x1522 | 2 | Int32 | 5 |  | R | Serialnumber
5412 | 0x1524 | 1 | Int16 | 5 |  | RW | Firmware minor version
5413 | 0x1525 | 1 | Int16 | 5 |  | RW | Firmware major version
5414 | 0x1526 | 2 | Int32 | 5 |  | R | Status word
5416 | 0x1528 | 2 | Int32 | 5 |  | R | Last reading
5418 | 0x152A | 1 | Int16 | 5 |  | RW | Channel A slot id, write 1 to blink led, 0 to clear any blinking led
5419 | 0x152B | 1 | Int16 | 5 |  | RW | Channel B slot id, write 1 to blink led, 0 to clear any blinking led
5420 | 0x152C | 1 | Int16 | 5 |  | RW | Channel C slot id, write 1 to blink led, 0 to clear any blinking led
5421 | 0x152D | 1 | Int16 | 5 |  | RW | Channel D slot id, write 1 to blink led, 0 to clear any blinking led
5422 | 0x152E | 1 | Int16 | 5 |  | RW | Channel E slot id, write 1 to blink led, 0 to clear any blinking led
5423 | 0x152F | 1 | Int16 | 5 |  | RW | Channel F slot id, write 1 to blink led, 0 to clear any blinking led
5424 | 0x1530 | 1 | Int16 | 5 |  | RW | Channel G slot id, write 1 to blink led, 0 to clear any blinking led
5425 | 0x1531 | 1 | Int16 | 5 |  | RW | Channel H slot id, write 1 to blink led, 0 to clear any blinking led
5426 | 0x1532 | 1 | Int16 | 5 |  | R | Firmware upgrade status
5427 | 0x1533 | 1 | Int16 | 5 |  | RW | Channel I slot id, write 1 to blink led, 0 to clear any blinking led
5428 | 0x1534 | 1 | Int16 | 5 |  | RW | Channel J slot id, write 1 to blink led, 0 to clear any blinking led
5429 | 0x1535 | 1 | Int16 | 5 |  | RW | Channel K slot id, write 1 to blink led, 0 to clear any blinking led
5430 | 0x1536 | 1 | Int16 | 5 |  | RW | Channel L slot id, write 1 to blink led, 0 to clear any blinking led
5431 | 0x1537 | 1 | Int16 | 5 |  | RW | Channel M slot id, write 1 to blink led, 0 to clear any blinking led
5432 | 0x1538 | 1 | Int16 | 5 |  | RW | Channel N slot id, write 1 to blink led, 0 to clear any blinking led
5433 | 0x1539 | 1 | Int16 | 5 |  | RW | Channel O slot id, write 1 to blink led, 0 to clear any blinking led
5434 | 0x153A | 1 | Int16 | 5 |  | RW | Channel P slot id, write 1 to blink led, 0 to clear any blinking led
5440 | 0x1540 | 1 | Int16 | 6 |  | RW | Device Type, write 1 to remove device
5441 | 0x1541 | 1 | Int16 | 6 |  | R | Number of assigned slots
5442 | 0x1542 | 2 | Int32 | 6 |  | R | Serialnumber
5444 | 0x1544 | 1 | Int16 | 6 |  | RW | Firmware minor version
5445 | 0x1545 | 1 | Int16 | 6 |  | RW | Firmware major version
5446 | 0x1546 | 2 | Int32 | 6 |  | R | Status word
5448 | 0x1548 | 2 | Int32 | 6 |  | R | Last reading
5450 | 0x154A | 1 | Int16 | 6 |  | RW | Channel A slot id, write 1 to blink led, 0 to clear any blinking led
5451 | 0x154B | 1 | Int16 | 6 |  | RW | Channel B slot id, write 1 to blink led, 0 to clear any blinking led
5452 | 0x154C | 1 | Int16 | 6 |  | RW | Channel C slot id, write 1 to blink led, 0 to clear any blinking led
5453 | 0x154D | 1 | Int16 | 6 |  | RW | Channel D slot id, write 1 to blink led, 0 to clear any blinking led
5454 | 0x154E | 1 | Int16 | 6 |  | RW | Channel E slot id, write 1 to blink led, 0 to clear any blinking led
5455 | 0x154F | 1 | Int16 | 6 |  | RW | Channel F slot id, write 1 to blink led, 0 to clear any blinking led
5456 | 0x1550 | 1 | Int16 | 6 |  | RW | Channel G slot id, write 1 to blink led, 0 to clear any blinking led
5457 | 0x1551 | 1 | Int16 | 6 |  | RW | Channel H slot id, write 1 to blink led, 0 to clear any blinking led
5458 | 0x1552 | 1 | Int16 | 6 |  | R | Firmware upgrade status
5459 | 0x1553 | 1 | Int16 | 6 |  | RW | Channel I slot id, write 1 to blink led, 0 to clear any blinking led
5460 | 0x1554 | 1 | Int16 | 6 |  | RW | Channel J slot id, write 1 to blink led, 0 to clear any blinking led
5461 | 0x1555 | 1 | Int16 | 6 |  | RW | Channel K slot id, write 1 to blink led, 0 to clear any blinking led
5462 | 0x1556 | 1 | Int16 | 6 |  | RW | Channel L slot id, write 1 to blink led, 0 to clear any blinking led
5463 | 0x1557 | 1 | Int16 | 6 |  | RW | Channel M slot id, write 1 to blink led, 0 to clear any blinking led
5464 | 0x1558 | 1 | Int16 | 6 |  | RW | Channel N slot id, write 1 to blink led, 0 to clear any blinking led
5465 | 0x1559 | 1 | Int16 | 6 |  | RW | Channel O slot id, write 1 to blink led, 0 to clear any blinking led
5466 | 0x155A | 1 | Int16 | 6 |  | RW | Channel P slot id, write 1 to blink led, 0 to clear any blinking led
5472 | 0x1560 | 1 | Int16 | 7 |  | RW | Device Type, write 1 to remove device
5473 | 0x1561 | 1 | Int16 | 7 |  | R | Number of assigned slots
5474 | 0x1562 | 2 | Int32 | 7 |  | R | Serialnumber
5476 | 0x1564 | 1 | Int16 | 7 |  | RW | Firmware minor version
5477 | 0x1565 | 1 | Int16 | 7 |  | RW | Firmware major version
5478 | 0x1566 | 2 | Int32 | 7 |  | R | Status word
5480 | 0x1568 | 2 | Int32 | 7 |  | R | Last reading
5482 | 0x156A | 1 | Int16 | 7 |  | RW | Channel A slot id, write 1 to blink led, 0 to clear any blinking led
5483 | 0x156B | 1 | Int16 | 7 |  | RW | Channel B slot id, write 1 to blink led, 0 to clear any blinking led
5484 | 0x156C | 1 | Int16 | 7 |  | RW | Channel C slot id, write 1 to blink led, 0 to clear any blinking led
5485 | 0x156D | 1 | Int16 | 7 |  | RW | Channel D slot id, write 1 to blink led, 0 to clear any blinking led
5486 | 0x156E | 1 | Int16 | 7 |  | RW | Channel E slot id, write 1 to blink led, 0 to clear any blinking led
5487 | 0x156F | 1 | Int16 | 7 |  | RW | Channel F slot id, write 1 to blink led, 0 to clear any blinking led
5488 | 0x1570 | 1 | Int16 | 7 |  | RW | Channel G slot id, write 1 to blink led, 0 to clear any blinking led
5489 | 0x1571 | 1 | Int16 | 7 |  | RW | Channel H slot id, write 1 to blink led, 0 to clear any blinking led
5490 | 0x1572 | 1 | Int16 | 7 |  | R | Firmware upgrade status
5491 | 0x1573 | 1 | Int16 | 7 |  | RW | Channel I slot id, write 1 to blink led, 0 to clear any blinking led
5492 | 0x1574 | 1 | Int16 | 7 |  | RW | Channel J slot id, write 1 to blink led, 0 to clear any blinking led
5493 | 0x1575 | 1 | Int16 | 7 |  | RW | Channel K slot id, write 1 to blink led, 0 to clear any blinking led
5494 | 0x1576 | 1 | Int16 | 7 |  | RW | Channel L slot id, write 1 to blink led, 0 to clear any blinking led
5495 | 0x1577 | 1 | Int16 | 7 |  | RW | Channel M slot id, write 1 to blink led, 0 to clear any blinking led
5496 | 0x1578 | 1 | Int16 | 7 |  | RW | Channel N slot id, write 1 to blink led, 0 to clear any blinking led
5497 | 0x1579 | 1 | Int16 | 7 |  | RW | Channel O slot id, write 1 to blink led, 0 to clear any blinking led
5498 | 0x157A | 1 | Int16 | 7 |  | RW | Channel P slot id, write 1 to blink led, 0 to clear any blinking led
5504 | 0x1580 | 1 | Int16 | 8 |  | RW | Device Type, write 1 to remove device
5505 | 0x1581 | 1 | Int16 | 8 |  | R | Number of assigned slots
5506 | 0x1582 | 2 | Int32 | 8 |  | R | Serialnumber
5508 | 0x1584 | 1 | Int16 | 8 |  | RW | Firmware minor version
5509 | 0x1585 | 1 | Int16 | 8 |  | RW | Firmware major version
5510 | 0x1586 | 2 | Int32 | 8 |  | R | Status word
5512 | 0x1588 | 2 | Int32 | 8 |  | R | Last reading
5514 | 0x158A | 1 | Int16 | 8 |  | RW | Channel A slot id, write 1 to blink led, 0 to clear any blinking led
5515 | 0x158B | 1 | Int16 | 8 |  | RW | Channel B slot id, write 1 to blink led, 0 to clear any blinking led
5516 | 0x158C | 1 | Int16 | 8 |  | RW | Channel C slot id, write 1 to blink led, 0 to clear any blinking led
5517 | 0x158D | 1 | Int16 | 8 |  | RW | Channel D slot id, write 1 to blink led, 0 to clear any blinking led
5518 | 0x158E | 1 | Int16 | 8 |  | RW | Channel E slot id, write 1 to blink led, 0 to clear any blinking led
5519 | 0x158F | 1 | Int16 | 8 |  | RW | Channel F slot id, write 1 to blink led, 0 to clear any blinking led
5520 | 0x1590 | 1 | Int16 | 8 |  | RW | Channel G slot id, write 1 to blink led, 0 to clear any blinking led
5521 | 0x1591 | 1 | Int16 | 8 |  | RW | Channel H slot id, write 1 to blink led, 0 to clear any blinking led
5522 | 0x1592 | 1 | Int16 | 8 |  | R | Firmware upgrade status
5523 | 0x1593 | 1 | Int16 | 8 |  | RW | Channel I slot id, write 1 to blink led, 0 to clear any blinking led
5524 | 0x1594 | 1 | Int16 | 8 |  | RW | Channel J slot id, write 1 to blink led, 0 to clear any blinking led
5525 | 0x1595 | 1 | Int16 | 8 |  | RW | Channel K slot id, write 1 to blink led, 0 to clear any blinking led
5526 | 0x1596 | 1 | Int16 | 8 |  | RW | Channel L slot id, write 1 to blink led, 0 to clear any blinking led
5527 | 0x1597 | 1 | Int16 | 8 |  | RW | Channel M slot id, write 1 to blink led, 0 to clear any blinking led
5528 | 0x1598 | 1 | Int16 | 8 |  | RW | Channel N slot id, write 1 to blink led, 0 to clear any blinking led
5529 | 0x1599 | 1 | Int16 | 8 |  | RW | Channel O slot id, write 1 to blink led, 0 to clear any blinking led
5530 | 0x159A | 1 | Int16 | 8 |  | RW | Channel P slot id, write 1 to blink led, 0 to clear any blinking led
5536 | 0x15A0 | 1 | Int16 | 9 |  | RW | Device Type, write 1 to remove device
5537 | 0x15A1 | 1 | Int16 | 9 |  | R | Number of assigned slots
5538 | 0x15A2 | 2 | Int32 | 9 |  | R | Serialnumber
5540 | 0x15A4 | 1 | Int16 | 9 |  | RW | Firmware minor version
5541 | 0x15A5 | 1 | Int16 | 9 |  | RW | Firmware major version
5542 | 0x15A6 | 2 | Int32 | 9 |  | R | Status word
5544 | 0x15A8 | 2 | Int32 | 9 |  | R | Last reading
5546 | 0x15AA | 1 | Int16 | 9 |  | RW | Channel A slot id, write 1 to blink led, 0 to clear any blinking led
5547 | 0x15AB | 1 | Int16 | 9 |  | RW | Channel B slot id, write 1 to blink led, 0 to clear any blinking led
5548 | 0x15AC | 1 | Int16 | 9 |  | RW | Channel C slot id, write 1 to blink led, 0 to clear any blinking led
5549 | 0x15AD | 1 | Int16 | 9 |  | RW | Channel D slot id, write 1 to blink led, 0 to clear any blinking led
5550 | 0x15AE | 1 | Int16 | 9 |  | RW | Channel E slot id, write 1 to blink led, 0 to clear any blinking led
5551 | 0x15AF | 1 | Int16 | 9 |  | RW | Channel F slot id, write 1 to blink led, 0 to clear any blinking led
5552 | 0x15B0 | 1 | Int16 | 9 |  | RW | Channel G slot id, write 1 to blink led, 0 to clear any blinking led
5553 | 0x15B1 | 1 | Int16 | 9 |  | RW | Channel H slot id, write 1 to blink led, 0 to clear any blinking led
5554 | 0x15B2 | 1 | Int16 | 9 |  | R | Firmware upgrade status
5555 | 0x15B3 | 1 | Int16 | 9 |  | RW | Channel I slot id, write 1 to blink led, 0 to clear any blinking led
5556 | 0x15B4 | 1 | Int16 | 9 |  | RW | Channel J slot id, write 1 to blink led, 0 to clear any blinking led
5557 | 0x15B5 | 1 | Int16 | 9 |  | RW | Channel K slot id, write 1 to blink led, 0 to clear any blinking led
5558 | 0x15B6 | 1 | Int16 | 9 |  | RW | Channel L slot id, write 1 to blink led, 0 to clear any blinking led
5559 | 0x15B7 | 1 | Int16 | 9 |  | RW | Channel M slot id, write 1 to blink led, 0 to clear any blinking led
5560 | 0x15B8 | 1 | Int16 | 9 |  | RW | Channel N slot id, write 1 to blink led, 0 to clear any blinking led
5561 | 0x15B9 | 1 | Int16 | 9 |  | RW | Channel O slot id, write 1 to blink led, 0 to clear any blinking led
5562 | 0x15BA | 1 | Int16 | 9 |  | RW | Channel P slot id, write 1 to blink led, 0 to clear any blinking led

## Bus Diagnostics
Modbus Address | Modbus Address (Hex) | Size | Type | Channel | Unit | R/W | Description
2304 | 0x0900 | 2 | Int32 | 0 |  | RW | high byte: frames received count in last second, low byte: sync received count in last second. Write 1 to blink LED , 0 to clear blink
2306 | 0x0902 | 2 | Int32 | 1 |  | RW | high byte: frames received count in last second, low byte: sync received count in last second. Write 1 to blink LED , 0 to clear blink
2308 | 0x0904 | 2 | Int32 | 2 |  | RW | high byte: frames received count in last second, low byte: sync received count in last second. Write 1 to blink LED , 0 to clear blink
2310 | 0x0906 | 2 | Int32 | 3 |  | RW | high byte: frames received count in last second, low byte: sync received count in last second. Write 1 to blink LED , 0 to clear blink
2312 | 0x0908 | 2 | Int32 | 4 |  | RW | high byte: frames received count in last second, low byte: sync received count in last second. Write 1 to blink LED , 0 to clear blink
2314 | 0x090A | 2 | Int32 | 5 |  | RW | high byte: frames received count in last second, low byte: sync received count in last second. Write 1 to blink LED , 0 to clear blink
2316 | 0x090C | 2 | Int32 | 6 |  | RW | high byte: frames received count in last second, low byte: sync received count in last second. Write 1 to blink LED , 0 to clear blink
2318 | 0x090E | 2 | Int32 | 7 |  | RW | high byte: frames received count in last second, low byte: sync received count in last second. Write 1 to blink LED , 0 to clear blink
2320 | 0x0910 | 2 | Int32 | 8 |  | RW | high byte: frames received count in last second, low byte: sync received count in last second. Write 1 to blink LED , 0 to clear blink
2322 | 0x0912 | 2 | Int32 | 9 |  | RW | high byte: frames received count in last second, low byte: sync received count in last second. Write 1 to blink LED , 0 to clear blink
2324 | 0x0914 | 2 | Int32 | 10 |  | RW | high byte: frames received count in last second, low byte: sync received count in last second. Write 1 to blink LED , 0 to clear blink
2326 | 0x0916 | 2 | Int32 | 11 |  | RW | high byte: frames received count in last second, low byte: sync received count in last second. Write 1 to blink LED , 0 to clear blink
2328 | 0x0918 | 2 | Int32 | 12 |  | RW | high byte: frames received count in last second, low byte: sync received count in last second. Write 1 to blink LED , 0 to clear blink
2330 | 0x091A | 2 | Int32 | 13 |  | RW | high byte: frames received count in last second, low byte: sync received count in last second. Write 1 to blink LED , 0 to clear blink
2332 | 0x091C | 2 | Int32 | 14 |  | RW | high byte: frames received count in last second, low byte: sync received count in last second. Write 1 to blink LED , 0 to clear blink
2334 | 0x091E | 2 | Int32 | 15 |  | RW | high byte: frames received count in last second, low byte: sync received count in last second. Write 1 to blink LED , 0 to clear blink
2336 | 0x0920 | 2 | Int32 | 16 |  | RW | high byte: frames received count in last second, low byte: sync received count in last second. Write 1 to blink LED , 0 to clear blink
2338 | 0x0922 | 2 | Int32 | 17 |  | RW | high byte: frames received count in last second, low byte: sync received count in last second. Write 1 to blink LED , 0 to clear blink
2340 | 0x0924 | 2 | Int32 | 18 |  | RW | high byte: frames received count in last second, low byte: sync received count in last second. Write 1 to blink LED , 0 to clear blink
2342 | 0x0926 | 2 | Int32 | 19 |  | RW | high byte: frames received count in last second, low byte: sync received count in last second. Write 1 to blink LED , 0 to clear blink
2344 | 0x0928 | 2 | Int32 | 20 |  | RW | high byte: frames received count in last second, low byte: sync received count in last second. Write 1 to blink LED , 0 to clear blink
2346 | 0x092A | 2 | Int32 | 21 |  | RW | high byte: frames received count in last second, low byte: sync received count in last second. Write 1 to blink LED , 0 to clear blink
2348 | 0x092C | 2 | Int32 | 22 |  | RW | high byte: frames received count in last second, low byte: sync received count in last second. Write 1 to blink LED , 0 to clear blink
2350 | 0x092E | 2 | Int32 | 23 |  | RW | high byte: frames received count in last second, low byte: sync received count in last second. Write 1 to blink LED , 0 to clear blink
2352 | 0x0930 | 2 | Int32 | 24 |  | RW | high byte: frames received count in last second, low byte: sync received count in last second. Write 1 to blink LED , 0 to clear blink
2354 | 0x0932 | 2 | Int32 | 25 |  | RW | high byte: frames received count in last second, low byte: sync received count in last second. Write 1 to blink LED , 0 to clear blink
2356 | 0x0934 | 2 | Int32 | 26 |  | RW | high byte: frames received count in last second, low byte: sync received count in last second. Write 1 to blink LED , 0 to clear blink
2358 | 0x0936 | 2 | Int32 | 27 |  | RW | high byte: frames received count in last second, low byte: sync received count in last second. Write 1 to blink LED , 0 to clear blink
2368 | 0x0940 | 1 | Int16 |  |  | R | performance indicator

## Firmware Management (hidden)
Modbus Address | Modbus Address (Hex) | Size | Type | Offset | R/W | Description
20480 | 0x5000 | 2 | Int32 |  | RW | Image length in bytes
20482 | 0x5002 | 2 | Int32 |  | RW | Offset
20484 | 0x5004 | 1 | Int16 |  | RW | Available buffer size in bytes
20544 | 0x5040 | 1 | Int16 | 0 | RW | Transfer Buffer
20545 | 0x5041 | 1 | Int16 | 1 | RW | Transfer Buffer
20546 | 0x5042 | 1 | Int16 | 2 | RW | Transfer Buffer
20547 | 0x5043 | 1 | Int16 | 3 | RW | Transfer Buffer
20548 | 0x5044 | 1 | Int16 | 4 | RW | Transfer Buffer
20549 | 0x5045 | 1 | Int16 | 5 | RW | Transfer Buffer
20550 | 0x5046 | 1 | Int16 | 6 | RW | Transfer Buffer
20551 | 0x5047 | 1 | Int16 | 7 | RW | Transfer Buffer
20552 | 0x5048 | 1 | Int16 | 8 | RW | Transfer Buffer
20553 | 0x5049 | 1 | Int16 | 9 | RW | Transfer Buffer
20554 | 0x504A | 1 | Int16 | 10 | RW | Transfer Buffer
20555 | 0x504B | 1 | Int16 | 11 | RW | Transfer Buffer
20556 | 0x504C | 1 | Int16 | 12 | RW | Transfer Buffer
20557 | 0x504D | 1 | Int16 | 13 | RW | Transfer Buffer
20558 | 0x504E | 1 | Int16 | 14 | RW | Transfer Buffer
20559 | 0x504F | 1 | Int16 | 15 | RW | Transfer Buffer
20560 | 0x5050 | 1 | Int16 | 16 | RW | Transfer Buffer
20561 | 0x5051 | 1 | Int16 | 17 | RW | Transfer Buffer
20562 | 0x5052 | 1 | Int16 | 18 | RW | Transfer Buffer
20563 | 0x5053 | 1 | Int16 | 19 | RW | Transfer Buffer
20564 | 0x5054 | 1 | Int16 | 20 | RW | Transfer Buffer
20565 | 0x5055 | 1 | Int16 | 21 | RW | Transfer Buffer
20566 | 0x5056 | 1 | Int16 | 22 | RW | Transfer Buffer
20567 | 0x5057 | 1 | Int16 | 23 | RW | Transfer Buffer
20568 | 0x5058 | 1 | Int16 | 24 | RW | Transfer Buffer
20569 | 0x5059 | 1 | Int16 | 25 | RW | Transfer Buffer
20570 | 0x505A | 1 | Int16 | 26 | RW | Transfer Buffer
20571 | 0x505B | 1 | Int16 | 27 | RW | Transfer Buffer
20572 | 0x505C | 1 | Int16 | 28 | RW | Transfer Buffer
20573 | 0x505D | 1 | Int16 | 29 | RW | Transfer Buffer
20574 | 0x505E | 1 | Int16 | 30 | RW | Transfer Buffer
20575 | 0x505F | 1 | Int16 | 31 | RW | Transfer Buffer
20576 | 0x5060 | 1 | Int16 | 32 | RW | Transfer Buffer
20577 | 0x5061 | 1 | Int16 | 33 | RW | Transfer Buffer
20578 | 0x5062 | 1 | Int16 | 34 | RW | Transfer Buffer
20579 | 0x5063 | 1 | Int16 | 35 | RW | Transfer Buffer
20580 | 0x5064 | 1 | Int16 | 36 | RW | Transfer Buffer
20581 | 0x5065 | 1 | Int16 | 37 | RW | Transfer Buffer
20582 | 0x5066 | 1 | Int16 | 38 | RW | Transfer Buffer
20583 | 0x5067 | 1 | Int16 | 39 | RW | Transfer Buffer
20584 | 0x5068 | 1 | Int16 | 40 | RW | Transfer Buffer
20585 | 0x5069 | 1 | Int16 | 41 | RW | Transfer Buffer
20586 | 0x506A | 1 | Int16 | 42 | RW | Transfer Buffer
20587 | 0x506B | 1 | Int16 | 43 | RW | Transfer Buffer
20588 | 0x506C | 1 | Int16 | 44 | RW | Transfer Buffer
20589 | 0x506D | 1 | Int16 | 45 | RW | Transfer Buffer
20590 | 0x506E | 1 | Int16 | 46 | RW | Transfer Buffer
20591 | 0x506F | 1 | Int16 | 47 | RW | Transfer Buffer
20592 | 0x5070 | 1 | Int16 | 48 | RW | Transfer Buffer
20593 | 0x5071 | 1 | Int16 | 49 | RW | Transfer Buffer
20594 | 0x5072 | 1 | Int16 | 50 | RW | Transfer Buffer
20595 | 0x5073 | 1 | Int16 | 51 | RW | Transfer Buffer
20596 | 0x5074 | 1 | Int16 | 52 | RW | Transfer Buffer
20597 | 0x5075 | 1 | Int16 | 53 | RW | Transfer Buffer
20598 | 0x5076 | 1 | Int16 | 54 | RW | Transfer Buffer
20599 | 0x5077 | 1 | Int16 | 55 | RW | Transfer Buffer
20600 | 0x5078 | 1 | Int16 | 56 | RW | Transfer Buffer
20601 | 0x5079 | 1 | Int16 | 57 | RW | Transfer Buffer
20602 | 0x507A | 1 | Int16 | 58 | RW | Transfer Buffer
20603 | 0x507B | 1 | Int16 | 59 | RW | Transfer Buffer
20604 | 0x507C | 1 | Int16 | 60 | RW | Transfer Buffer
20605 | 0x507D | 1 | Int16 | 61 | RW | Transfer Buffer
20606 | 0x507E | 1 | Int16 | 62 | RW | Transfer Buffer
20607 | 0x507F | 1 | Int16 | 63 | RW | Transfer Buffer
65000 | 0xFDE8 | 1 | Int16 |  | RW | Write 1 to save config to flash
65001 | 0xFDE9 | 1 | Int16 |  | RW | Reserved
65002 | 0xFDEA | 1 | Int16 |  | R | Device status
65003 | 0xFDEB | 1 | Int16 |  | R | Firmware upgrade status
65004 | 0xFDEC | 1 | Int16 |  | RW | Device type | Registers 65004 to 65007 are only available on configuration address 62
65005 | 0xFDED | 2 | Int32 |  | RW | Device serial
65007 | 0xFDEF | 1 | Int16 |  | RW | Modbus Address